DIVISION 9 – FINISHES

SECTION 09780 SEAMLESS EPOXY-QUARTZ FLOORING

ARMOR-REZ CQ 600

- GENERAL REQUIREMENTS

  - WORK INCLUDED

    - Provide labor, equipment, and materials to complete a resinous flooring application and installation suitable and compliant for the specific use indicated in the contract documents on horizontal concrete.  The objective of this specification is achieved with the installation of a system of resinous flooring with multiple components consisting of the following, applied directly to a concrete substrate:

      - Patching, filling, and moisture vapor {as needed} with APF Epoxy 300 Flex Paste, APF Vapor Solve System.

      - 1st Basecoat: APF Epoxy 600

      - Broadcast 1: APF Color Quartz

      - 2nd Basecoat: APF Epoxy 600

      - Broadcast 2: APF Color Quartz

      - Topcoat: APF Epoxy 600 or Epoxy 900

      - Optional 2nd Topcoat: APF Polyurethane 100/100 VOC

  - RELATED SECTIONS

    - Specified elsewhere:

      - Section 03 30 00 Cast in Place Concrete

      - Section 09 00 00 Finishes

    - References:

      - ASTM C-579 Compressive Strength

      - ASTM C-307 Tensile Strength

      - ASTM C-580 Flexural Strength

      - ASTM D-2240 Hardness, Shore D

      - ASTM D-2794 Impact Resistance

      - ASTM D-4060 Abrasion Resistance

      - ASTM E-648 Flammability

      - ASTM F-1679 Coefficient of friction

    - Notes to Users of this Document {e.g., Architects Engineers, Designers, and Consulting Professionals:

      - This specification is supplied in an exhaustive format with the intent of achieving as comprehensive an inclusion of project factors as possible.

      - The specifier is NOT obligated to utilize this specification in its entirety but instead is encouraged to adopt/adapt/apply those provisions which apply to specific projects.

      - All construction projects are unique.  Ultimately, it is the responsibility of the involved parties (e.g., Installer/Applicator, Remediator/Restorer, General Contractor, Owner, Client, Enforcement Authority, Architect, Engineer or Consultant) to verify on a case-by-case basis that applications of this specification are appropriate.

      - Deviation: Certain projects will involve unavoidable circumstances that prevent project execution in full accord with industry professional standards of care, and the tenets of this specification.  A separate and specific specification should be developed in consultation with all parties, including product manufacturers, when deviation is the only option for achieving the property owner's objectives.

      - Where contradicted by federal, state, or local laws and regulations, any of the preceding supplants the information in this document.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Acceptable Manufacturer: ICP Construction, Arizona Polymer Flooring {APF}; 150 Dascomb Rd., Andover, MA 01810

    - Single Source Responsibility: Obtain all product system components from a single manufacturer with not less than 20 years of successful experience in manufacturing and specifying the installation of the principal materials described in this specification.  Provide secondary/supplementary materials only of the type and from a source recommended by the manufacturer of the primary material(s).

    - Contractor/Applicator Experience: The installer shall be a firm or individual experienced with the objectives of this specification.

      - The installer must have a minimum of 3 years’ experience in installing the polymeric flooring system(s) specified and be approved by the manufacturer.

    - Sampling of Materials: When directed by Architect/Engineer, obtain test samples from material stored at the project site or source of supply (distributor or manufacturer.

    - Mock-Up: Upon request (By Owner, Client, Enforcement Authority, Assessor, Architect or Engineer), it may be determined necessary to provide a mock-up for evaluation of surface preparation techniques, validation of performance expectations, and anticipated application workmanship.

      - The applicator shall make and submit a sample of the proposed finish to the architect and/or owner for approval.

      - Do not proceed with remaining work until pertinent project authority (By Owner, Client, Enforcement Authority, Assessor, Architect or Engineer), approves the mock-up.

  - SUBMITTALS (as directed to Owner, Client, Enforcement Authority, Assessor, Architect, Engineer or Consultant)

    - Submit under the provisions of Section 013300.

    - Submit the Manufacturer’s product data sheets for each product and system data sheets for the applicable system to be used.

    - Submit electronically Manufacturer’s Safety Data Sheets (SDS).  Content of VOCs shall not exceed pertinent regulations regarding VOCs.

    - Submit the Manufacturer’s maintenance instructions/guidelines.

NOTES:

      - Bidders are encouraged to submit materials that meet the Basis of Design.  To have material accepted as approved for the work outlined herein, the alternate or substitute proposed must be received by the architect for evaluation and approval no less than 21 days before the original published bid date.  Approved alternate products will be by Addendum only. Submittals circumventing this process will not be approved and will not be acceptable for inclusion in this project.

      - Substitutions will only be considered for products manufactured by companies of primarily U.S. ownership.

  - PRODUCT DELIVERY, STORAGE AND HANLDING

    - Deliver manufacturer's unopened containers to the work site. Packaging shall bear the manufacturer's name, label, and product number.

    - Storage of Materials:

      - Store only acceptable project materials on site.

      - Store in a suitable and secure location convenient to progress work.

      - Comply with health and fire regulations.  No products listed in the Basis of Design are flammable or combustible.

      - Storage temperatures shall be between 50° F (10 °C) and 85° F (30 °C), or such other ambient temperature conditions as may be specifically recommended by the product manufacturer.

      - Products shall not be permitted to freeze on site, and delivery should be refused if freezing during transit is probable.

      - Avoid storage directly in hot sun exposures or excessive temperatures.

      - Keep containers tightly closed when not in use.

      - Store securely closed and upright in the original container. Lids or caps can leak if containers are placed on their sides.

      - Keep out of reach of children.

    - Handling:

      - Dispose of materials in accordance with the requirements of local authorities having jurisdiction.

      - Verify that products are within acceptable shelf life, and do not utilize any product that is older than the maximum shelf life stated by the manufacturer.

    - Extra Materials:

      - Furnish extra coating materials in the quantities agreed in advance. Package with protective covering for storage and label with descriptions of contents. Deliver extra materials to the Owner. OR,

      - Furnish Owner with sufficient additional coating to address an additional one percent overall surface area, but not less than 1 gal. (3.8 l), 5 gal. pail (19 l), or 1 case, as appropriate and collectively agreed upon in advance of substantial completion.

  - JOB SITE CONDITIONS

    - Environmental requirements:

      - Comply with manufacturers’ recommendations as to environmental conditions under which all chemicals and coatings can be applied.

        - Temperature: Do not apply products at temperatures beyond the limits stated in the manufacturer’s technical data sheet unless given written permission by the manufacturer.

      - Surface/Substrate Moisture:

        - Moisture more than 85% contact Arizona Polymer Flooring.

        - Consult manufacturer regarding whether topical dampness (latent moisture tangible by touch) after wet cleaning or recent precipitation is acceptable at the time of application of coatings, or if a completely dry (absence of above-normal topical and subsurface moisture) surface is required.  Applicators are expected to account for slow-drying surface elements (such as shaded areas, hairline cracks, nail holes).

        - Before applying, measure and ensure that the ambient temperature is at least 5°F above the dew point.

    - Surface Protection/Prevention of Cross-Contamination:

      - Cover or otherwise protect adjacent areas.  Identify adjacent areas that could be cross-contaminated by construction activity.

      - Careful attention should be paid to any occupied areas in the vicinity of the work area.

      - Utilize adequate engineering controls to ensure worker and occupant safety and health and prevent cross-contamination.  Engineering controls may include, but are not limited to, source containment, isolation barriers, pressure differentials, dust suppression, and high-efficiency particulate air (HEPA) vacuuming and filtration.

    - Provide adequate illumination and ventilation.

    - The applicator shall have access to electrical power, clean potable water, and a clean work area at the location where the materials are to be applied/installed.

- PRODUCTS

  - MATERIALS {Basis of Design}

    - ICP Construction/Arizona Polymer Flooring {APF} or its authorized distributors shall supply all products.

    - Substitutions or additions of other materials will void the warranty.

    - Armor-Rez CQ 600 is a 3/16th inch thick decorative color quartz flooring system using a chemical-resistant epoxy throughout. It offers excellent abrasion, impact and chemical resistance.

    - Components:

      - APF Epoxy 600: 2-component, low viscosity, 100% solid epoxy.

      - Optional APF Epoxy 900: 2-component, 100% solid epoxy.

      - Optional APF Polyurethane 100/100 VOC: 2-component aliphatic polyurethane

      - APF Color Quartz: decorative aggregate.

    - Accessories:

      - APF Epoxy 300 Flex Paste {if needed}: 2-component 100% solids, medium viscosity, flexible epoxy product.

      - APF VaporSolve System {if needed}: specially formulated 2-component product kits designed to isolate the concrete from moisture-sensitive flooring.

  - COLORS

    - Reference the Arizona Polymer Flooring {APF} Color Charts for available standard colors.  If a custom color is required, contact Arizona Polymer Flooring {APF} Technical Services for additional information.

  - MIXING

    - Mix all products in accordance with the manufacturer’s instructions on individual product data sheets.

- EXECUTION

  - EXAMINATION

    - Verification of Conditions:

      - Inspect surfaces to receive the floor system.

      - Conduct a concrete moisture test in accordance with ASTM F2170-19, consult Arizona Polymer Flooring Technical Service before proceeding if results indicate moisture to be more than 85%.

      - Before starting work, report in writing to the Architect about any unsatisfactory conditions.

      - The application of any material shall signify that surfaces have been inspected and are satisfactory to receive the specified flooring system.

  - PREPARATION OF WORKSITE, SURFACES

    - Concrete must be cured for at least 30 days, be clean, structurally sound, and free of wax, loose coatings, or curing compounds. Concrete should be properly prepared to achieve a surface Minimum Texture of ICRI/CSP 2-3. Refer to ICRI technical guidelines 310-330, Selecting and specifying concrete surface preparation for sealer, coatings, polymer overlays, and concrete repair. Vacuum the prepared concrete surface to remove all dust. Acid etching is not recommended and will void the manufacturer’s warranty.

  - GENERAL SURFACE PREPARATION INSTRUCTIONS FOR ALL SUBSTRATES

    - Concrete Moisture: If moisture is indicated to be more than 85%, apply APF VaporSolve system in accordance with the published system data sheet and recommendations from APF Technical Service Team.

    - Crack Repair: After the initial preparation has been completed, inspect the surface for indentations and holes. These must be filled before application using Epoxy 300 Flex Paste.  Refer to APF Epoxy 300 Flex Paste Product Data Sheet, or Armor-Rez CQ 600 System Data Sheet and Application Instructions Section 3.0 Crack Repair for instructions.

  - APPLICATION

    - Allow sufficient time for the installation of the flooring system. At no time shall the speed of project completion be allowed to affect the application detrimentally.

    - Provide sufficient light, power, heat and working conditions to permit proper application of the materials. The ambient air and surface temperature shall be a minimum of 50°F (10°C) and a maximum of 85°F (30°C) and shall remain so for at least 24 hours.

    - Application of 1st Basecoat:

      - After mixing Epoxy 600 according to the product data sheet, apply Epoxy 600 onto the surface immediately after mixing with a squeegee, back roll using a quality solvent-resistant 3/8-inch nap roller cover. Apply at a rate of 32 sq. ft./gallon at 50 mils WFT.

      - A “wet edge” is recommended when applying the product; do not attempt to roll over material that has begun to set. An applicator wearing spiked shoes will back roll the wet material using a quality solvent-resistant 3/8-inch nap roller cover to distribute the material uniformly. The material must be thoroughly rolled twice to achieve optimal substrate wetting {using North-South, East-West Method.}.

      - Apply a second coat, if necessary, within 24 hour recoat window. If the recoat window is exceeded, the surface must be abraded with 80-100 grit to a uniform gloss free and dust free texture prior to recoat.

      - For Broadcast 1: APF Color Quarts application at 0.75 lbs/sqft to refusal.

    - Application of 2nd Basecoat:

      - After mixing Epoxy 600 according to the product data sheet, apply Epoxy 600 onto the surface immediately after mixing with a squeegee, back roll using a quality solvent-resistant 3/8-inch nap roller cover. Apply at a rate of 80 sq. ft./gallon at 20 mils WFT.

      - A “wet edge” is recommended when applying the product; do not attempt to roll over material that has begun to set. An applicator wearing spiked shoes will back roll the wet material using a quality solvent-resistant 3/8-inch nap roller cover to distribute the material uniformly. The material must be thoroughly rolled twice to achieve optimal substrate wetting {using North-South, East-West Method.}.

      - For Broadcast 2: APF Color Quarts application at 0.75 lbs/sqft to refusal.

    - Application of Topcoat:

      - After mixing Epoxy 600 according to the product data sheet, apply Epoxy 600 onto the surface immediately after mixing with a squeegee, back roll using a quality solvent-resistant 3/8-inch nap roller cover. Apply at a rate of 80-160 sq. ft./gallon at 10-20 mils WFT.

      - A “wet edge” is recommended when applying the product; do not attempt to roll over material that has begun to set. An applicator wearing spiked shoes will back roll the wet material using a quality solvent-resistant 3/8-inch nap roller cover to distribute the material uniformly. The material must be thoroughly rolled twice to achieve optimal substrate wetting {using North-South, East-West Method.}.

      - Apply a second coat, if necessary, within 24 hour recoat window. If the recoat window is exceeded, the surface must be abraded with 80-100 grit to a uniform gloss free and dust free texture prior to recoat.

    - Optional Application of Topcoat:

      - After mixing Epoxy 900 according to the product data sheet, apply Epoxy 900 onto the surface immediately after mixing with a squeegee, back roll using a quality solvent-resistant 3/8-inch nap roller cover. Apply at a rate of 80-160 sq. ft./gallon at 10-20 mils WFT.

      - A “wet edge” is recommended when applying the product; do not attempt to roll over material that has begun to set. An applicator wearing spiked shoes will back roll the wet material using a quality solvent-resistant 3/8-inch nap roller cover to distribute the material uniformly. The material must be thoroughly rolled twice to achieve optimal substrate wetting {using North-South, East-West Method.}.

      - Apply a second coat, if necessary, within 24 hour recoat window. If the recoat window is exceeded, the surface must be abraded with 80-100 grit to a uniform gloss free and dust free texture prior to recoat.

    - Optional 2nd Topcoat Application

      - After mixing Polyurethane 100/100 VOC according to the product data sheet, apply it to the surface immediately after mixing with a squeegee or roller, back roll using a quality solvent-resistant 3/8-inch nap roller cover. Apply at a rate of 250-300 sq. ft./gallon at 5-6 mils WFT.

      - A “wet edge” is recommended when applying the product; do not attempt to roll over material that has begun to set. An applicator wearing spiked shoes will back roll the wet material using a quality solvent-resistant 3/8-inch nap roller cover to distribute the material uniformly. The material must be thoroughly rolled twice to achieve optimal substrate wetting {using North-South, East-West Method.}.

    - Field Quality Control:

      - The installer shall monitor the thickness of the system as the work progresses. Areas found not to meet the required thickness shall be addressed accordingly to meet the required system thickness.

    - Protection:

      - Installation areas must be kept free from traffic and other trades during the application procedure and cure time.

      - Prohibit traffic on the floor for 48 hours after installation.  Avoid heavy abrasion and chemical exposure for 7 days after installation.  Allow 72 hours minimum for vehicular traffic.

  - CLEANING

    - Remove the remaining debris promptly from the work area and dispose of it properly.

    - Remove spilled, splashed, or splattered coating materials from all surfaces.

    - Do not mar the surface finish of items being cleaned.

    - Clean up tools and other equipment with warm, soapy water before coating dries.

    - Review product labels for proper disposal of unused products and empty containers.

  - MAINTENANCE

    - The contractor shall provide maintenance and cleaning instructions for the floor system upon completion to the owner or party designated by the owner.  The owner is responsible for maintaining and cleaning the surface as required by the warranty.

    - Contact Arizona Polymer Flooring (APF) Technical Services for additional information regarding proper cleaning and maintenance procedures based on the specified system installed.

    - Refer to the APF Cleaning & Maintenance for New Floor Systems guide at www.apfepoxy.com.

  - SLIP AND FALL PRECAUTIONS

    - OSHA, American Disabilities Act (ADA), and the Federal Housing Act (FHA) have now set enforceable standards for slip-resistance on pedestrian surfaces.  ICP Construction/Arizona Polymer Flooring {APF} recommends the use of angular slip-resistant aggregate in all coatings or flooring systems that may be exposed to wet, oily/greasy, or otherwise potentially slippery conditions.  It is the end user’s responsibility to provide a flooring system that meets current safety standards.  ICP Construction/Arizona Polymer Flooring {APF} or its sales agents will not be responsible for injury incurred in a slip and fall accident. Please consult local building codes for the current coefficient of friction requirement.

  - WARRANTY

    - The manufacturer shall guarantee that this material shall be free from defects and comply with published specifications.

      - Extent of warranty shall be limited to the repair or replacement of defective surfaces at no cost to the Owner, and for any damage directly resulting from such defects during the warranty period of one (1) year.  The warranty shall not include any remedy for repair labor, or for defects caused by abuse, improper maintenance or operation, or by normal wear, tear and usage.  Contact the manufacturer for the entire warranty.  This section is informative only and does not constitute a warranty.

    - Installer shall provide the Owner, through Assessor, Architect/Engineer, with an acceptable form of warranty against defects in workmanship for one (1) year from the date of substantial completion.