## Table F13
Natutal Gas - Flow Through - Copper Pipe (NZS 3501) (MJ/h)
(Pressure drop of 1.5 kPa; suitable for supply pressures within the range 5-10 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
10 | 189 | 130 | 104 | 89 | 79 | 72 | 66 | 61 | 58
15 | 405 | 297 | 224 | 191 | 170 | 154 | 141 | 132 | 123
20 | 1166 | 801 | 643 | 551 | 488 | 442 | 407 | 379 | 355
25 | 2497 | 1716 | 1378 | 1179 | 1045 | 947 | 871 | 811 | 761
32 | 4502 | 3094 | 2484 | 2126 | 1885 | 1708 | 1571 | 1464 | 1371
40 | 7232 | 4971 | 3992 | 3416 | 3028 | 2743 | 2524 | 2348 | 2203
50 | 15381 | 10571 | 8489 | 7265 | 6439 | 5834 | 5368 | 4993 | 4685
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
10 | 54 | 48 | 44 | 40 | 37 | 34 | 33 | 32 | 30
15 | 117 | 103 | 94 | 86 | 80 | 75 | 71 | 67 | 64
20 | 335 | 297 | 269 | 248 | 231 | 216 | 204 | 194 | 185
25 | 718 | 637 | 577 | 531 | 494 | 463 | 438 | 416 | 397
32 | 1295 | 1148 | 1040 | 957 | 890 | 835 | 835 | 749 | 715
40 | 2081 | 1844 | 1671 | 1537 | 1430 | 1342 | 1342 | 1204 | 1149
50 | 4426 | 3922 | 3554 | 3270 | 3042 | 2854 | 2854 | 2560 | 2443
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
10 | 29 | 28 | 27 | 26 | 25 | 24 | 24 | 19 | 16
15 | 62 | 59 | 57 | 55 | 53 | 52 | 49 | 44 | 41
20 | 177 | 170 | 164 | 158 | 153 | 149 | 140 | 127 | 177
25 | 380 | 365 | 351 | 339 | 328 | 318 | 301 | 273 | 251
32 | 685 | 658 | 634 | 612 | 592 | 574 | 542 | 491 | 452
40 | 110 | 1057 | 1018 | 983 | 951 | 922 | 871 | 789 | 726
50 | 2339 | 2247 | 2165 | 2091 | 2023 | 1961 | 1853 | 1679 | 1544
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
10 | 14 | 13 | 11 | 10
15 | 38 | 36 | 34 | 32 | 30 | 28 | 26 | 24 | 23
20 | 109 | 102 | 97 | 92 | 87 | 84 | 80 | 78 | 75
25 | 233 | 219 | 207 | 196 | 187 | 197 | 172 | 166 | 160
32 | 421 | 395 | 373 | 354 | 338 | 323 | 311 | 299 | 289
40 | 676 | 634 | 599 | 569 | 543 | 520 | 499 | 481 | 464
50 | 1437 | 1348 | 1273 | 1209 | 1154 | 1154 | 1061 | 1023 | 988
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F12
Natutal Gas - Flow Through - Copper Pipe (NZS 3501) (MJ/h)
(Pressure drop of 0.75 kPa; suitable for supply pressures within the range 2.75-5 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
10 | 130 | 89 | 72 | 61 | 54 | 79 | 45 | 42 | 40
15 | 279 | 191 | 154 | 132 | 117 | 106 | 97 | 90 | 85
20 | 801 | 551 | 442 | 379 | 335 | 304 | 280 | 260 | 244
25 | 1716 | 1179 | 947 | 811 | 718 | 651 | 599 | 557 | 523
32 | 3094 | 2126 | 1708 | 1461 | 1295 | 1174 | 1080 | 1004 | 942
40 | 4971 | 3416 | 2743 | 2348 | 2081 | 1885 | 1735 | 1614 | 1514
50 | 10571 | 7265 | 5834 | 5993 | 4426 | 4010 | 3689 | 3432 | 3220
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
10 | 37 | 33 | 30 | 28 | 26 | 24 | 23 | 21 | 19
15 | 80 | 71 | 64 | 59 | 55 | 52 | 49 | 46 | 44
20 | 231 | 204 | 185 | 170 | 158 | 149 | 140 | 133 | 127
25 | 494 | 438 | 397 | 465 | 339 | 318 | 301 | 286 | 273
32 | 890 | 789 | 715 | 658 | 612 | 574 | 542 | 515 | 491
40 | 1430 | 1268 | 1149 | 1057 | 983 | 922 | 871 | 827 | 789
50 | 3042 | 2696 | 2443 | 2247 | 2091 | 1961 | 1853 | 1760 | 1679
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
10 | 18 | 16 | 15 | 14 | 13 | 13 | 11
15 | 42 | 41 | 39 | 38 | 37 | 36 | 34 | 30 | 26
20 | 122 | 117 | 113 | 109 | 105 | 102 | 97 | 87 | 80
25 | 261 | 251 | 242 | 233 | 226 | 219 | 207 | 187 | 172
32 | 471 | 452 | 435 | 421 | 407 | 395 | 373 | 338 | 311
40 | 756 | 726 | 700 | 676 | 654 | 634 | 599 | 543 | 499
50 | 1608 | 1544 | 1488 | 1437 | 1390 | 1348 | 1273 | 1154 | 1061
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
10
15 | 23 | 20 | 18 | 17 | 15 | 14 | 13 | 12 | 11
20 | 75 | 70 | 66 | 63 | 60 | 58 | 55 | 53 | 51
25 | 160 | 150 | 142 | 135 | 129 | 123 | 118 | 114 | 110
32 | 289 | 271 | 256 | 243 | 232 | 222 | 214 | 206 | 199
40 | 464 | 436 | 412 | 391 | 373 | 357 | 343 | 330 | 319
50 | 988 | 927 | 875 | 831 | 793 | 759 | 730 | 703 | 679
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F11
Natutal Gas - Flow Through - Copper Pipe (NZS 3501) (MJ/h)
(Pressure drop of 0.25 kPa; suitable for supply pressures within the range 1.5-2.5 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
10 | 72 | 49 | 40 | 34 | 30 | 27 | 25 | 23 | 21
15 | 754 | 106 | 85 | 73 | 64 | 58 | 54 | 50 | 47
20 | 442 | 304 | 244 | 209 | 185 | 168 | 154 | 144 | 135
25 | 947 | 651 | 523 | 449 | 397 | 359 | 331 | 307 | 289
32 | 1708 | 1174 | 942 | 807 | 715 | 648 | 596 | 554 | 520
40 | 2743 | 1885 | 1514 | 1296 | 1149 | 1041 | 957 | 891 | 836
50 | 5734 | 4010 | 3220 | 2759 | 2443 | 2213 | 2036 | 1894 | 1777
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
10 | 19 | 15 | 13 | 11
15 | 44 | 39 | 36 | 33 | 30 | 27 | 24 | 22 | 20
20 | 127 | 113 | 102 | 94 | 87 | 82 | 78 | 75 | 70
25 | 273 | 242 | 219 | 201 | 187 | 176 | 166 | 158 | 150
32 | 491 | 435 | 395 | 363 | 338 | 317 | 299 | 284 | 271
40 | 789 | 700 | 634 | 583 | 543 | 509 | 481 | 457 | 436
50 | 1679 | 1488 | 1348 | 1240 | 1154 | 1083 | 1023 | 971 | 927
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
10
15 | 19 | 17 | 16 | 15 | 14 | 13 | 12 | 10
20 | 67 | 65 | 62 | 60 | 28 | 56 | 53 | 48 | 43
25 | 144 | 138 | 133 | 129 | 125 | 121 | 114 | 103 | 95
32 | 260 | 249 | 240 | 232 | 225 | 218 | 206 | 186 | 171
40 | 417 | 401 | 386 | 373 | 361 | 350 | 220 | 299 | 275
50 | 887 | 852 | 821 | 793 | 767 | 744 | 703 | 637 | 586
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
10
15
20 | 38 | 34 | 30 | 28 | 25 | 23 | 22 | 20 | 19
25 | 88 | 83 | 78 | 75 | 71 | 68 | 65 | 63 | 61
32 | 160 | 150 | 141 | 134 | 128 | 123 | 118 | 114 | 110
40 | 256 | 240 | 227 | 216 | 206 | 197 | 189 | 182 | 176
50 | 545 | 511 | 483 | 459 | 438 | 419 | 403 | 388 | 375
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F10
Natutal Gas - Flow Through - Copper Pipe (NZS 3501) (MJ/h)
(Pressure drop of 0.25 kPa; suitable for supply pressures within the range 1.5-2.5 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
10 | 48 | 33 | 27 | 23 | 18 | 15 | 13 | 11 | 10
15 | 103 | 71 | 57 | 49 | 43 | 39 | 36 | 34 | 31
20 | 297 | 204 | 164 | 140 | 124 | 113 | 104 | 97 | 91
25 | 637 | 438 | 351 | 301 | 267 | 242 | 222 | 207 | 194
32 | 1148 | 789 | 634 | 542 | 481 | 435 | 401 | 373 | 350
40 | 1844 | 1268 | 1018 | 871 | 772 | 700 | 644 | 599 | 562
50 | 3922 | 2696 | 2165 | 1853 | 1642 | 1488 | 1369 | 1273 | 1195
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
10
15 | 29 | 23 | 19 | 17 | 15 | 13 | 12 | 11
20 | 86 | 76 | 69 | 63 | 59 | 55 | 52 | 49 | 47
25 | 183 | 162 | 147 | 135 | 126 | 118 | 112 | 106 | 101
32 | 330 | 293 | 265 | 244 | 227 | 213 | 201 | 191 | 182
40 | 531 | 470 | 426 | 392 | 365 | 342 | 323 | 307 | 293
50 | 1129 | 1000 | 906 | 834 | 776 | 728 | 687 | 653 | 623
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
10
15
20 | 45 | 42 | 39 | 36 | 34 | 32 | 29 | 24 | 21
25 | 97 | 93 | 90 | 87 | 84 | 81 | 77 | 69 | 64
32 | 175 | 168 | 162 | 156 | 151 | 146 | 138 | 125 | 115
40 | 280 | 269 | 260 | 251 | 243 | 235 | 222 | 201 | 185
50 | 597 | 573 | 552 | 533 | 516 | 500 | 473 | 428 | 394
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
10
15
20 | 18 | 16 | 15 | 13 | 12 | 11 | 10
25 | 58 | 52 | 47 | 42 | 39 | 36 | 33 | 31 | 29
32 | 107 | 101 | 95 | 90 | 86 | 82 | 79 | 76 | 72
40 | 172 | 162 | 153 | 145 | 138 | 132 | 127 | 123 | 118
50 | 366 | 344 | 325 | 308 | 294 | 282 | 271 | 261 | 252
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F9
Natutal Gas - Flow Through - Copper Pipe (AS 1432 Type B) (MJ/h)
(Pressure drop of 1.5 kPa; suitable for supply pressures within the range 5-10 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
15 | 244 | 168 | 135 | 115 | 102 | 93 | 85 | 79 | 74
20 | 807 | 554 | 445 | 381 | 338 | 306 | 281 | 262 | 246
25 | 1772 | 1218 | 978 | 837 | 742 | 672 | 619 | 575 | 540
32 | 3399 | 2336 | 1876 | 1606 | 1423 | 1289 | 1186 | 1104 | 1035
40 | 5720 | 3931 | 3157 | 2702 | 2394 | 2170 | 1996 | 1857 | 1742
50 | 13161 | 9046 | 7264 | 6217 | 5510 | 4993 | 4593 | 4273 | 4009
65 | 24377 | 16754 | 13454 | 11515 | 10206 | 9247 | 5807 | 7914 | 7426
80 | 38760 | 26639 | 21392 | 18309 | 16227 | 14703 | 13526 | 12584 | 11807
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
20 | 232 | 206 | 186 | 171 | 160 | 150 | 141 | 134 | 128
25 | 510 | 452 | 410 | 377 | 351 | 329 | 311 | 295 | 281
32 | 978 | 767 | 875 | 723 | 672 | 631 | 596 | 566 | 540
40 | 1646 | 1459 | 1322 | 1216 | 1131 | 1061 | 1002 | 952 | 908
50 | 3787 | 3356 | 3041 | 2798 | 2603 | 2442 | 2307 | 2191 | 2090
65 | 7014 | 6217 | 5633 | 5182 | 4821 | 4523 | 4273 | 4058 | 3871
80 | 11153 | 9884 | 8956 | 8239 | 7665 | 6794 | 6794 | 6452 | 6155
100 | 24649 | 21846 | 19794 | 18210 | 16941 | 15015 | 15015 | 14260 | 13604
125 | 45174 | 40037 | 36276 | 33374 | 31048 | 27517 | 27517 | 26134 | 24932
150 | 72663 | 64400 | 58351 | 53682 | 49941 | 44262 | 44262 | 42037 | 40104
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
15 | 37 | 36 | 34 | 33 | 32 | 31 | 29 | 27 | 24
20 | 123 | 118 | 114 | 110 | 106 | 103 | 97 | 88 | 81
25 | 270 | 259 | 249 | 241 | 233 | 226 | 214 | 193 | 178
32 | 517 | 497 | 478 | 462 | 447 | 433 | 409 | 371 | 341
40 | 870 | 836 | 805 | 777 | 752 | 729 | 689 | 624 | 574
50 | 2002 | 1923 | 1852 | 1789 | 1731 | 1687 | 1585 | 1437 | 1322
65 | 3707 | 3562 | 3431 | 3313 | 3206 | 3109 | 2937 | 2661 | 2448
80 | 5895 | 5663 | 5455 | 5268 | 5098 | 4943 | 4669 | 4231 | 3892
100 | 13028 | 12516 | 12057 | 11644 | 11268 | 10925 | 10320 | 9350 | 8602
125 | 23876 | 22938 | 22097 | 21339 | 20650 | 20022 | 18912 | 17136 | 15765
150 | 38405 | 36896 | 3554 | 34324 | 33217 | 32205 | 30421 | 27564 | 25358
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
25 | 166 | 155 | 147 | 139 | 133 | 127 | 122 | 118 | 114
32 | 318 | 298 | 281 | 267 | 255 | 244 | 235 | 226 | 218
40 | 534 | 501 | 474 | 450 | 429 | 511 | 395 | 380 | 367
50 | 1229 | 1154 | 1090 | 1035 | 987 | 945 | 908 | 875 | 845
65 | 2277 | 2137 | 2018 | 1917 | 1829 | 1751 | 1682 | 1621 | 1565
80 | 3621 | 3379 | 3209 | 3048 | 2908 | 2784 | 2657 | 2577 | 2489
100 | 8003 | 7509 | 7093 | 6736 | 6426 | 6154 | 5912 | 5696 | 5500
125 | 14666 | 13761 | 12998 | 12345 | 11777 | 11278 | 10835 | 10438 | 10080
150 | 23591 | 22135 | 20908 | 19857 | 18944 | 18141 | 17429 | 16790 | 16214
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F8
Natutal Gas - Flow Through - Copper Pipe (AS 1432 Type B) (MJ/h)
(Pressure drop of 0.75 kPa; suitable for supply pressures within the range 2.75-5 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
15 | 168 | 115 | 93 | 79 | 70 | 64 | 59 | 54 | 51
20 | 554 | 381 | 306 | 262 | 232 | 210 | 193 | 180 | 169
25 | 1218 | 837 | 672 | 575 | 510 | 462 | 425 | 396 | 371
32 | 2336 | 1606 | 1289 | 1104 | 978 | 886 | 815 | 758 | 712
40 | 3931 | 2702 | 2170 | 1857 | 1646 | 1491 | 1372 | 1276 | 1197
50 | 9049 | 6217 | 4993 | 4273 | 3787 | 3431 | 3157 | 2937 | 2755
65 | 16754 | 11515 | 9247 | 7914 | 7014 | 6355 | 5847 | 5439 | 5104
80 | 26639 | 18309 | 14703 | 12584 | 11153 | 10105 | 9297 | 8649 | 8115
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
15 | 48 | 43 | 39 | 36 | 33 | 31 | 29 | 28 | 27
20 | 160 | 141 | 128 | 118 | 110 | 103 | 97 | 92 | 88
25 | 351 | 311 | 281 | 259 | 241 | 226 | 214 | 203 | 193
32 | 672 | 596 | 540 | 497 | 462 | 433 | 409 | 389 | 371
40 | 1131 | 1002 | 908 | 836 | 777 | 729 | 689 | 654 | 624
50 | 2603 | 2307 | 2090 | 1923 | 1789 | 1678 | 1585 | 1506 | 1437
65 | 4821 | 4273 | 3871 | 3562 | 3313 | 3109 | 2937 | 2789 | 2661
80 | 7665 | 6794 | 6155 | 5663 | 5268 | 4943 | 4669 | 4435 | 4231
100 | 16941 | 15015 | 13604 | 12516 | 11644 | 10925 | 10320 | 9801 | 9350
125 | 31048 | 27517 | 27932 | 22938 | 21339 | 20022 | 18912 | 17962 | 17136
150 | 49941 | 44262 | 40104 | 36896 | 34324 | 32205 | 30421 | 28892 | 27564
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
20 | 84 | 81 | 78 | 75 | 73 | 71 | 67 | 61 | 56
25 | 185 | 178 | 171 | 166 | 160 | 155 | 147 | 133 | 122
32 | 355 | 431 | 329 | 318 | 307 | 298 | 281 | 255 | 235
40 | 598 | 574 | 553 | 534 | 517 | 501 | 474 | 429 | 395
50 | 1376 | 1322 | 1273 | 1229 | 1190 | 1154 | 1090 | 987 | 908
65 | 2548 | 2448 | 2358 | 2277 | 2204 | 2137 | 2018 | 1829 | 1682
80 | 4051 | 3892 | 3750 | 3621 | 3504 | 2297 | 3209 | 2908 | 2675
100 | 8954 | 8602 | 8287 | 8003 | 7744 | 7509 | 7093 | 6426 | 5912
125 | 16410 | 15765 | 15187 | 14666 | 14193 | 13761 | 12998 | 11777 | 10835
150 | 26395 | 25358 | 24429 | 23591 | 22830 | 22135 | 20908 | 18944 | 17429
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
25 | 114 | 107 | 101 | 96 | 91 | 88 | 84 | 81 | 78
32 | 218 | 205 | 193 | 184 | 175 | 168 | 161 | 155 | 150
40 | 367 | 345 | 325 | 309 | 295 | 282 | 271 | 261 | 252
50 | 845 | 793 | 749 | 711 | 679 | 650 | 624 | 601 | 581
65 | 1565 | 1469 | 1387 | 1317 | 1257 | 1204 | 1156 | 1114 | 1076
80 | 2489 | 2335 | 2206 | 2095 | 1998 | 1914 | 1839 | 1771 | 1710
100 | 5500 | 5161 | 4875 | 4630 | 4417 | 4230 | 4063 | 3915 | 3780
125 | 10080 | 9458 | 8934 | 8485 | 8095 | 7752 | 7447 | 7174 | 6928
150 | 16214 | 15213 | 14370 | 13648 | 13020 | 12469 | 11989 | 11540 | 11144
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F7
Natutal Gas - Flow Through - Copper Pipe (AS 1432 Type B) (MJ/h)
(Pressure drop of 0.25 kPa; suitable for supply pressures within the range 1.5-2.5 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
15 | 93 | 64 | 51 | 44 | 39 | 35 | 32 | 30 | 28
20 | 306 | 210 | 169 | 145 | 128 | 116 | 107 | 99 | 93
25 | 672 | 462 | 371 | 318 | 281 | 255 | 235 | 218 | 205
32 | 1289 | 886 | 712 | 609 | 540 | 489 | 450 | 419 | 393
40 | 2170 | 1491 | 1197 | 1025 | 908 | 823 | 757 | 704 | 661
50 | 4993 | 3431 | 2755 | 2358 | 2090 | 1894 | 1742 | 1621 | 1521
65 | 9247 | 6355 | 5104 | 4368 | 3871 | 3508 | 3227 | 3002 | 2817
80 | 14703 | 10105 | 8115 | 6945 | 6155 | 5577 | 5131 | 4773 | 4479
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
20 | 88 | 78 | 71 | 65 | 61 | 57 | 54 | 51 | 49
25 | 193 | 171 | 155 | 143 | 133 | 125 | 118 | 112 | 109
32 | 371 | 329 | 298 | 274 | 255 | 239 | 226 | 215 | 205
40 | 624 | 553 | 501 | 461 | 429 | 403 | 380 | 361 | 345
50 | 1437 | 1273 | 1154 | 1061 | 987 | 926 | 875 | 831 | 793
65 | 2661 | 2358 | 2137 | 1966 | 1829 | 1716 | 1621 | 1539 | 1469
80 | 4231 | 3750 | 3397 | 3125 | 2908 | 2728 | 2577 | 2448 | 2335
100 | 9350 | 8287 | 7509 | 6908 | 6426 | 6030 | 5696 | 5409 | 5161
125 | 17136 | 15187 | 13761 | 12660 | 11777 | 11050 | 10438 | 9914 | 9458
150 | 27564 | 24429 | 22135 | 20363 | 18944 | 17775 | 16790 | 15946 | 15213
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
20 | 47 | 45 | 43 | 42 | 40 | 38 | 35 | 29 | 25
25 | 102 | 98 | 95 | 91 | 88 | 86 | 81 | 73 | 68
32 | 196 | 188 | 181 | 175 | 170 | 164 | 155 | 141 | 129
40 | 330 | 317 | 305 | 295 | 285 | 277 | 261 | 237 | 218
50 | 759 | 729 | 703 | 679 | 657 | 637 | 601 | 545 | 501
65 | 1406 | 1351 | 1302 | 1257 | 1216 | 1216 | 1114 | 1009 | 929
80 | 2236 | 2148 | 2069 | 1998 | 1998 | 1934 | 1771 | 1605 | 1476
100 | 4942 | 4748 | 4574 | 4417 | 4417 | 4274 | 3915 | 3547 | 3263
125 | 9057 | 8701 | 8382 | 8095 | 7833 | 7833 | 7174 | 6500 | 5980
150 | 14568 | 13996 | 1343 | 13020 | 12600 | 12600 | 11540 | 10456 | 9619
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
25 | 63 | 59 | 56 | 52 | 48 | 44 | 41 | 38 | 36
32 | 120 | 113 | 107 | 101 | 97 | 93 | 89 | 86 | 83
40 | 203 | 190 | 180 | 171 | 163 | 156 | 150 | 144 | 139
50 | 466 | 438 | 413 | 393 | 375 | 359 | 345 | 332 | 321
65 | 864 | 811 | 766 | 727 | 694 | 664 | 638 | 615 | 594
80 | 1374 | 1289 | 1217 | 1156 | 1103 | 1056 | 1015 | 978 | 944
100 | 3036 | 2848 | 2690 | 2555 | 2438 | 2334 | 2243 | 2161 | 2086
125 | 5563 | 5220 | 4931 | 4683 | 4468 | 4278 | 4110 | 3960 | 3824
150 | 8949 | 8396 | 7931 | 7533 | 7186 | 6882 | 6611 | 6369 | 6150
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general

## Table F6
Natutal Gas - Flow Through - Copper Pipe (AS 1432 Type B) (MJ/h)
(Pressure drop of 0.12 kPa; suitable for supply pressures within the range 1.25 kPa)
Nom. Dia DN | Length of straight pipe in metres
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18
15 | 62 | 43 | 34 | 29 | 26 | 22 | 19 | 17 | 15
20 | 206 | 141 | 114 | 97 | 86 | 78 | 72 | 67 | 63
25 | 452 | 311 | 249 | 214 | 189 | 171 | 158 | 149 | 138
32 | 867 | 596 | 478 | 409 | 363 | 329 | 302 | 281 | 264
40 | 1459 | 1002 | 805 | 689 | 611 | 553 | 509 | 474 | 444
50 | 3356 | 2307 | 1852 | 1585 | 1405 | 1273 | 1171 | 1090 | 1022
65 | 6217 | 4273 | 3431 | 2937 | 2603 | 2358 | 2169 | 2018 | 1894
80 | 9884 | 6794 | 5455 | 4669 | 4138 | 3750 | 3450 | 3209 | 3011
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
20 | 59 | 52 | 48 | 44 | 41 | 37 | 33 | 30 | 28
25 | 130 | 115 | 104 | 96 | 89 | 84 | 79 | 75 | 72
32 | 249 | 221 | 200 | 184 | 171 | 161 | 152 | 144 | 138
40 | 420 | 372 | 337 | 310 | 288 | 271 | 256 | 243 | 232
50 | 966 | 856 | 776 | 713 | 664 | 623 | 588 | 559 | 533
65 | 1789 | 1585 | 1436 | 1321 | 1229 | 1154 | 1090 | 1035 | 987
80 | 2844 | 2551 | 2284 | 2101 | 1955 | 1834 | 1732 | 1645 | 1570
100 | 6286 | 5571 | 5048 | 4644 | 4320 | 4054 | 3829 | 3637 | 3469
125 | 11520 | 10210 | 9251 | 8411 | 7918 | 7429 | 7017 | 6665 | 6358
150 | 18531 | 16423 | 14881 | 13690 | 12736 | 11950 | 11288 | 10720 | 10227
| 65 | 70 | 75 | 80 | 85 | 90 | 100 | 120 | 140
25 | 69 | 66 | 64 | 61 | 59 | 58 | 54 | 46 | 39
32 | 132 | 127 | 122 | 118 | 114 | 111 | 104 | 95 | 87
40 | 222 | 213 | 205 | 198 | 192 | 186 | 176 | 159 | 146
50 | 510 | 490 | 472 | 456 | 441 | 428 | 404 | 366 | 337
65 | 945 | 908 | 875 | 848 | 818 | 793 | 749 | 679 | 624
80 | 1503 | 1444 | 1391 | 1344 | 1300 | 1261 | 1191 | 1079 | 993
100 | 3322 | 3192 | 3075 | 2969 | 2874 | 2786 | 2632 | 2384 | 2194
125 | 6089 | 5850 | 5635 | 5442 | 5266 | 5106 | 4823 | 4370 | 4020
150 | 9794 | 9409 | 9064 | 8753 | 8471 | 8213 | 7758 | 7029 | 6467
| 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320
32 | 81 | 76 | 72 | 68 | 62 | 57 | 53 | 50 | 47
40 | 136 | 128 | 121 | 115 | 109 | 105 | 101 | 97 | 94
50 | 314 | 294 | 278 | 264 | 252 | 241 | 232 | 223 | 215
65 | 581 | 545 | 515 | 489 | 466 | 447 | 429 | 412 | 399
80 | 923 | 866 | 818 | 777 | 742 | 710 | 682 | 657 | 635
100 | 2041 | 1915 | 1809 | 1718 | 1639 | 1569 | 1508 | 1452 | 1403
125 | 3740 | 3509 | 3315 | 3148 | 3003 | 3003 | 2763 | 2662 | 2571
150 | 6016 | 5645 | 5332 | 5064 | 4831 | 4831 | 4445 | 4282 | 4135
NOTE: Use of values in shaded areas is not receommended and require professional advice. Deliverable enrgy flow may be increase by 20% provided supply pressure and 1.5 times pressure drop can meet device minimum inlet pressure requirements. Refer to Paragraph F1 where further, detailed explaination is provided on these values and the use of tables in general