PART 1 GENERAL

1.01	GENERAL REQUIREMENTS

- Provide all materials, labor, equipment and services necessary to furnish, deliver and install all work under this section as shown on the contract documents, specified herein, and as specified by the job conditions.

1.02 	DESCRIPTION

- Related work specified elsewhere:

1. Metal Fabrication. 		Section 05 50 00

2. Rough Carpentry. 		Section 06 10 00

3. Access Panels & Doors:	Section 08 31 00

4. Painting:			Section 09 91 00

5. Electrical:			Division 26

1.03 	SUBMITTALS

- Procedures: Furnish submittals in accordance with the general requirements specified.

- Shop Drawing: Furnish shop drawings for architect's approval.  Include elevations, sections, and details indicating dimensions, materials, finishes, conditions for anchorage and support of each door.

- Certifications:

  - Submit manufacturer’s Underwriters Laboratories (UL), Warnock Hersey (WH) or Factory Mutual Research (FM) laboratory test report verifying product compliance in accordance with the required fire and smoke ratings.

  - Submit manufacturer’s Code Compliance Research Report published by an independent third-party testing agency that is certified by the International Accreditation Service confirming compliance of the fire door assembly in accordance with the International Building Code.

- Product Literature: Submit manufacturer's technical literature describing the product to be used under this section.

- Maintenance and Operating Manuals: Furnish complete manuals describing the materials, devices and procedures to be followed in operating and maintaining all doors under this section. Include manufacturer's brochures and parts lists describing the actual materials used in the product.

1.04 	QUALITY ASSURANCE

- Fire & Smoke Rated Assemblies: Provide all doors with fire and smoke resistance rating required to comply with governing regulations which are inspected, tested, listed and labeled by UL, WH or FM and complying with NFPA 80 for class of opening. Provide units tested in accordance with the requirements of UL 10B, UL 1784, NFPA 252, ASTM E-152. Provide testing laboratory label permanently fastened to each fire and smoke door assembly.

- Regulatory Requirements:

  - Comply with applicable requirements of the laws, codes, ordinances and regulations of federal, state and municipal authorities having jurisdiction.

  - Listed under a certified Code Compliance Research Report in accordance with the applicable sections of the International Building Code.

- Manufacturer Requirements: Door manufacturer shall have been in the business of and have experience in manufacturing the type of product covered under this specification section as well as giving credible service for a minimum of five (5) years. Provide list of at least ten (10) completed projects which include the products covered under this section.

1.05 	DELIVERY, STORAGE AND HANDLING

- General: Deliver and store materials in manufacturer's original packaging, labeled to show name, brand and type. Store materials in a protected dry location off the ground in accordance with manufacturer's instructions.

1.06 	WARRANTY

- Door Warranty: Provide Two (2) Year Warranty signed by the manufacturer and installer agreeing to repair or replace work which has failed as a result of defects in materials or workmanship. Upon notification within the warranty period, such defects shall be repaired at no cost to the owner.

PART 2 PRODUCTS

  - ACCORDION FIRE & SMOKE RATED DOORS WITH EGRESS

- Manufacturer: Accordion fire and smoke rated doors with egress shall be the Safescape Compact Pocket model AC8807CP-SS as manufactured by McKEON.

  - MATERIALS

- General: Each unit shall consist of an interlocking single folding panel curtain system suspended from a steel head track assembly and designed to be stored in a reduced size compact pocket. Curtain shall be designed to travel in a horizontal plane, smoothly and without binding and shall be driven to the open and close position by a positive action sprocket and integral endless drive chain system.

- Curtain Panels: Shall be fabricated of 18-gauge, stainless steel interlocking panels with an approximate cross section not greater than 7” wide.

- Leading Edge: Curtain shall be furnished with a stainless steel member of tubular design to provide stiffness, limit deflection and provide for a tight-fitting closure.

- Receiving Edge: Shall be fabricated of a stainless steel member with sufficient depth, designed to accept the leading edge and form a tight-fitting closure when the door is the fully closed position.

- Head Track: Shall be of not less than a 1/8" thick steel formed shape with stainless steel removable pans that conceal and protect the integral positive action endless drive chain system. The overall track width shall not be greater than 9”.

- Perimeter Smoke Seals: Provided perimeter smoke seals and sweeps as required to maintain smoke and draft rating in accordance with UL 1784 requirements. Sweeps shall be located at both the top and bottom ends of each curtain panel.

- Electric Motor Operator: Fire door shall be provided with a compact power unit mounted above the head track assembly for ease of accessibility and service. Operator shall be equipped with an adjustable limit switch to break the circuit at termination of travel. Operator is to be housed in a NEMA type 1 enclosure.

1. 	Motor: Shall be intermediate duty, thermally protected, ball bearing type with a class A or better insulation. Horsepower of motor is to be 1/3 hp minimum.

2. 	Starter: Shall be size "0" magnetic reversing starter, across the line type with mechanical and electrical interlocks, with 10-amp continuous rating and 24 volt control circuit.

3. 	Reducer: Planetary gear type, 80% efficiency minimum.

4. 	Brake: Magnetically activated, integral within the operator's housing.

5.	Remote Control Station: Provide flush mount key switch control station marked open, close and stop which shall be field wired to the operator’s control panel and mounted at a location as indicated on the contract drawings.

- Automatic Closing System: Listed in accordance with UL864 and designed to interface with the Fire and Alarm Control Panel and/or other fire alarm initiating devices. When activated by smoke detection or fire alarm the door shall be power driven to the fully closed position with the ability to open for egress by any building occupant, pause and re-close until the fire alarm system has been deactivated.  The automatic closing system shall consist of the following:

1.   Microprocessor-based electronic control center with the capability of performing the following:

- Monitor dual power sources to include:

  - Battery – Low or Failure

  - Charging Circuit Failure

  - Fuse Failures

  - Input Power

  - AC Failure

  - Monitor Inputs to include:

      - Brake

      - Clutch

      - Overload

      - Close Limit Contact

      - Motor Running

      - MCU Failure

      - Alarm Power Output

      - Sensing Device

      - Key Switch (optional)

      - 3-button Control Station (optional)

      - Function and Timer Display

      - Egress Touch Pad(s)

      - Sound Warning Alarms

- Egress Exit Device: Touch pad egress devices shall be located on both sides of fire door assembly. Activation of either egress device shall cause the fire door to power open to a pre-determined programmable distance, momentarily stop and then automatically return to the fully closed position.

- Master Control Station: Provide a single master control station that can simultaneously activate all of the fire rated doors in the facility or in a designated zone to the open or close positions. The master control station shall remain operable as long as there is no main power failure to the fire doors motor operators.

- Selectable Security Access Control Mode: The operating system shall allow for the fire door to also function as a security door. When the fire door is switched to the security access control mode, the fire door’s fire exit devices shall become inactivate and the door shall now be operable for authorized use only via the remote key switch control station or master control station. In the event of a fire emergency condition while the door is set in the security access control mode, a notification or signal from the facility’s fire alarm or smoke detection system shall automatically override the security access control mode feature and all of the fire exit devices shall immediately become active.

- Obstruction Sensing Device: The obstruction sensing safety edge shall be programable to either stop or reverse when coming in contact with an obstruction during the fire door’s closing cycle. During normal operation the obstruction sensing safety edge shall remain active and operable as long as there is a power supply to the motor operator. During an alarm condition, the obstruction sensing safety edge shall either stop or reverse a maximum of three times. If programmed to reverse, during the fourth  attempt to close if an obstruction still remains in the fire door’s path, the fire door shall come to rest on the obstruction until the obstruction has been removed and then the fire door shall continue to the fully closed position.

- (OPTION) True Test Panel: Fire door shall be provided with a True Test Switch. The test switch shall activate the fire door to close via gravity (not power) and shall be in accordance with NFPA Bulletin 80.

- (OPTION) Floor Track Assembly. Shall be no greater than ¾” deep, set flush with finish floor to maintain curtain rigidity as a method for mitigating air pressure resistance.

- (OPTION) Vision Panels: Each vision panel shall be no greater than 1-3/4” wide x 5-5/8” high in quantities and mounting location(s) as indicated in the contract drawings in accordance for building code compliance.

- (OPTION) Remote Monitoring: Provide remote monitoring interface to allow the fire door’s position of either fully open or fully closed to be monitored from the facility’s control room.

- Finish: After completion of fabrication, clean all metal surfaces to remove dirt. All steel components shall receive two coats of rust inhibitive primer. All exposed stainless steel components shall be of type 304 with number 4 polish finish.

PART 3 EXECUTION

3.01  	EXAMINATION

- Examine surfaces and field conditions to which this work is to be performed and notify architect if conditions of surfaces exist which are detrimental to proper installation and timely completion of work.

- Verify all dimensions taken at job site affecting the work. Notify the architect in any instance where dimensions vary.

- Coordinate and schedule work under this section with work of other sections so as not to delay job progress.

3.02  	INSTALLATION

- Perform installation using only factory approved and certified representatives of the door manufacturer.

- Install door assemblies at locations shown in perfect alignment and elevation, plumb, level, straight and true.

- Adjust door installation to provide uniform clearances and smooth non-binding operation.

- Install wiring in accordance with applicable local codes and the National Electrical Code Standard. Materials shall be UL listed.

- Test door closing sequence when activated by the building's fire alarm system.  Reset door after successful test.

3.03  	PROTECTION AND CLEANING

- Protect installed work using adequate and suitable means during and after installation until accepted by owner.

- Remove, repair or replace materials which have been damaged in any way.

- Clean surfaces of grime and dirt using acceptable and recommended means and methods.