SECTION 08 33 00

COILING SECURITY GRILLES (Heavy Duty / High Cycle)

PART 1 GENERAL

1.01
GENERAL REQUIREMENTS

A. Provide all materials, labor, equipment and services necessary to furnish, deliver and install all work under this section as shown on the contract documents, specified herein, and as specified by the job conditions.

1.02 
DESCRIPTION

A. Related work specified elsewhere:

1. Metal Fabrication. 

Section 05 50 00

2. Rough Carpentry. 

Section 06 10 00

3. Access Panels & Doors:
Section 08 31 00

4. Painting:


Section 09 91 00

5. Electrical:


Division 26

1.03 
SUBMITTALS

A. Procedures: Furnish submittals in accordance with the general requirements specified.
B. Shop Drawing: Furnish shop drawings for architect's approval.  Include elevations, sections, and details indicating dimensions, materials, finishes, conditions for anchorage and support of each coiling security grille.
C. Product Literature: Submit manufacturer's technical literature describing the product to be used under this section.
D. Maintenance and Operating Manuals: Furnish complete manuals describing the materials, devices and procedures to be followed in operating and maintaining all coiling security grilles under this section. Include manufacturer's brochures and parts lists describing the actual materials used in the product.

1.04 
QUALITY ASSURANCE

A. Regulatory Requirements: Comply with applicable requirements of the laws, codes, ordinances and regulations of federal, state and municipal authorities having jurisdiction.
B. Manufacturer Requirements: Coiling security grille manufacturer shall have been in the business of and have experience in manufacturing the type of product covered under this specification section as well as giving credible service for a minimum of five (5) years. Provide list of at least ten (10) completed projects which include the products covered under this section.

1.05 
DELIVERY, STORAGE AND HANDLING

A. General: Deliver and store materials in manufacturer's original packaging, labeled to show name, brand and type. Store materials in a protected dry location off the ground in accordance with manufacturer's instructions.

1.06 
WARRANTY

A. Coiling Security Grille Warranty: Provide Two (2) Year Warranty signed by the manufacturer and installer agreeing to repair or replace work which has failed as a result of defects in materials or workmanship. Upon notification within the warranty period, such defects shall be repaired at no cost to the owner.
PART 2 PRODUCTS

2.01 COILING SECURITY GRILLES

A. Manufacturer: Coiling security grilles shall be the model SG3000-SL9-ADF-SS as manufactured by McKeon Door Company.

2.02 MATERIALS

A. Curtain: Shall be the SL9 pattern consisting of 5/16" diameter solid aluminum rods encased by 3/8” stainless steel tubular spacers 9” long. The vertical links shall be fabricated of 1/16” x 5/8” stainless steel strips and shall be set in a straight lattice pattern. The vertical spacing shall be 9” and the horizontal spacing is 2”.

B. Bottom Bar: Shall consist of an extruded tubular section of not less than 1½” x 3" stainless steel formed to fit curtain and finished to match grille curtain. 

C. Guides: Each guide assembly shall be fabricated of a 3" x 3" steel support angle or tube, with a 2" x 3" inner guide stainless steel angle and a 3" x 3" outer guide stainless steel angle.
D. Mounting Brackets: Fabricated of hot rolled 3/16” steel plate minimum, brackets shall be provided to house ends of the counterbalance barrel assembly.
E. Hood: Shall be provided to entirely enclose curtain and counterbalance barrel assembly. Hood shall be fabricated 22 gauge stainless steel and designed to match brackets. Top and bottom shall be bent and reinforced for stiffness.
F. Counterbalance Assembly: Coiling security grille shall be counterbalanced by means of adjustable steel helical torsion springs attached to shaft enclosed in pipe with required mounting blocks or rings for attachment of curtain. Grease sealed bearings or self-lubricating graphite bearings shall be attached to the spring barrel which shall be fabricated of hot formed structural quality carbon steel seamless pipe.
G. Electric Motor Operator: Coiling security grille shall be provided with a direct drive power unit model type ADF. The operator shall not utilize any drive chains between the door's inner shaft and the motor operator, the drive shaft of the door shall run directly into the gearbox of the operator without the use of any drive chains or drive sprockets. High efficiency helical gearing running in an oil bath shall be furnished together with a rectifier-operated brake completely housed to protect against damage, dust, and moisture. An efficient overload protection device, which will break the power circuit and protect against damage to the motor windings shall be integral with the unit. The motor operator shall be designed to operate the door at an average speed of 6" per second. Operator is to be NEMA type 1 enclosure.
1. Motor: Shall be intermediate duty, thermally protected, ball bearing type with a class A or better insulation. Horsepower of motor is to be 3/4hp minimum or of manufacturer's recommended size, which ever is greater.
2. Starter: Shall be size "0" magnetic reversing starter, across the line type with mechanical and electrical interlocks, with 10 amp continuous rating and 24 volt control circuit.
3. Reducer: Heliacal gear type, 75% efficiency minimum.
4. Brake: Magnetically activated, integral within the operator's housing.
5. Control Station: Provide surface mount push button control station marked open, close and stop.
H. Obstruction Sensing Device: The coiling security grille shall be designed with an obstruction sensing safety edge. In the event that the safety edge meets an obstruction during the normal closing operation, the coiling security grille shall stop, reverse and return to the open position. 
I. Finish: After completion of fabrication, clean all metal surfaces to remove dirt. All steel components shall receive two coats of rust inhibitive primer. All exposed stainless steel components shall be of type 304 with a No. 4 polished finish.

PART 3 EXECUTION

3.01  
EXAMINATION

A. Examine surfaces and field conditions to which this work is to be performed and notify architect if conditions of surfaces exist which are detrimental to proper installation and timely completion of work.

B. Verify all dimensions taken at job site affecting the work. Notify the architect in any instance where dimensions vary.

C. Coordinate and schedule work under this section with work of other sections so as not to delay job progress.

3.02  
INSTALLATION

A. Perform installation using only factory approved and certified representatives of the coiling security grille manufacturer.

B. Install coiling security grille assemblies at locations shown in perfect alignment and elevation, plumb, level, straight and true.

C. Adjust coiling security grille installation to provide uniform clearances and smooth non-binding operation.

D. Install wiring in accordance with applicable local codes and the National Electrical Code Standard. Materials shall be UL listed.

3.03  
PROTECTION AND CLEANING

A. Protect installed work using adequate and suitable means during and after installation until accepted by owner.

B. Remove, repair or replace materials which have been damaged in any way.

C. Clean surfaces of grime and dirt using acceptable and recommended means and methods.

PAGE 2 of 3

