## i-45_V4.64
System Parameters - Read Only
| Modbus Address | Name | Format | Scale | Default | Description/Format
| 40001 | Serial Number Low | UINT16 | x1 |  | This is consistent with the original document. This is effectively little Endian UINT32
| 40002 | Serial Number High | UINT16 | x1 |  | This is consistent with the original document. This is effectively little Endian UINT32
| 40003 | Firmware Version | UINT16 | x1
| 40004 | OEM Identification | UINT16 | x1 |  | "PT" in ASCII
| 40005 | Meter Model | UINT16 | x1 | 45 | {109, 431, 636,45, 888}
| 40014 | Number of Curent Element on Unit | UINT16 | x1 | 45 | This is a maximum of 45 on the iMeter45
| 40015 | Number of Meters on Unit | UINT16 | x1 |  | For the MP636, this will be 6, 8, or 16, for the 5x3 phase (+1x1phase), 8x2phase, or 16x1 phase
| 40016 | Modbus Uptime | UINT32 | x1 |  | This is the number of seconds since the last power cycle on the modbus module.
| 40019 | Meter Config | UINT16 | x1 |  | The configuration of the meter
Configuration Parameters
| Modbus Address | Name | Format | Access | Default | Description/Format
| 41000 | PTRatio | UINT16 | R/W | 1 | The PT ratio that will be used in calculations. It does not affect meter operation.
41001
| 41002 | Address | UINT16 | R/W | 1 | Changes to the Modbus address take effect immediately. The next command must use the changed address, otherwise the module will not respond
| 41003 | Baud Rate | Enumated | R/W | 3 = 9600 bps | 3 = 9600 bps 4 = 19200 bps 5 = 38400 bps 6 = 57600 bps 7 = 115200 bps
| 41004 | CT Ratio - Meter 1 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41005 | CT Ratio - Meter 2 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41006 | CT Ratio - Meter 3 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41007 | CT Ratio - Meter 4 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41008 | CT Ratio - Meter 5 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41009 | CT Ratio - Meter 6 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41010 | CT Ratio - Meter 7 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41011 | CT Ratio - Meter 8 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41012 | CT Ratio - Meter 9 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41013 | CT Ratio - Meter 10 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41014 | CT Ratio - Meter 11 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41015 | CT Ratio - Meter 12 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41016 | CT Ratio - Meter 13 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41017 | CT Ratio - Meter 14 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41018 | CT Ratio - Meter 15 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41019 | CT Ratio - Meter 16 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41020 | Demand Intervals | Enumerated | R/W | 2 | 0 = 1 minute 1 = 5 minutes 2 = 15 minutes 3 = 30 minutes 4 = 60 minutes 5 = Disabled
| 41050 | CT Ratio - Meter 1 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41051 | CT Ratio - Meter 2 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41052 | CT Ratio - Meter 3 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41053 | CT Ratio - Meter 4 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41054 | CT Ratio - Meter 5 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41055 | CT Ratio - Meter 6 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41056 | CT Ratio - Meter 7 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41057 | CT Ratio - Meter 8 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41058 | CT Ratio - Meter 9 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41059 | CT Ratio - Meter 10 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41060 | CT Ratio - Meter 11 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41061 | CT Ratio - Meter 12 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41062 | CT Ratio - Meter 13 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41063 | CT Ratio - Meter 14 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41064 | CT Ratio - Meter 15 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41065 | CT Ratio - Meter 16 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41066 | CT Ratio - Meter 17 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41067 | CT Ratio - Meter 18 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41068 | CT Ratio - Meter 19 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41069 | CT Ratio - Meter 20 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41070 | CT Ratio - Meter 21 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41071 | CT Ratio - Meter 22 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41072 | CT Ratio - Meter 23 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41073 | CT Ratio - Meter 24 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41074 | CT Ratio - Meter 25 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41075 | CT Ratio - Meter 26 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41076 | CT Ratio - Meter 27 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41077 | CT Ratio - Meter 28 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41078 | CT Ratio - Meter 29 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41079 | CT Ratio - Meter 30 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41080 | CT Ratio - Meter 31 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41081 | CT Ratio - Meter 32 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41082 | CT Ratio - Meter 33 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41083 | CT Ratio - Meter 34 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41084 | CT Ratio - Meter 35 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41085 | CT Ratio - Meter 36 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41086 | CT Ratio - Meter 37 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41087 | CT Ratio - Meter 38 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41088 | CT Ratio - Meter 39 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41089 | CT Ratio - Meter 40 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41090 | CT Ratio - Meter 41 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41091 | CT Ratio - Meter 42 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 41092 | CT Ratio - Meter 43 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
Meter 1 Information
| Modbus Address | Name | Format | Unit | Default | Description/Format
| 41100 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 41101 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41103 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41105 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41107 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41109 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41111 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41113 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41115 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41117 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41119 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41121 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41123 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
41125
41127
41129
| 41131 | Power Factor A | INT32 | 0.001 Units
| 41133 | Power Factor B | INT32 | 0.001 Units
| 41135 | Power Factor C | INT32 | 0.001 Units
41137
41139
41141
| 41143 | kWh | UINT32 | Wh
| 41145 | kVAh | UINT32 | VAh
41147
| 41149 | Frequency | UINT32 | 0.01 Hz
41151
41153
| 41155 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 41157 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
41159
| 41161 | Meter Total Watts | UINT32 | 0.01 W
| 41163 | Meter Total VA | UINT32 | 0.01 VA
Meter 2 Information
| Modbus Address | Name | Format | Unit | Default | Description/Format
| 41200 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 41201 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41203 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41205 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41207 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41209 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41211 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41213 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41215 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41217 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41219 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41221 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41223 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
41225
41227
41229
| 41231 | Power Factor A | INT32 | 0.001 Units
| 41233 | Power Factor B | INT32 | 0.001 Units
| 41235 | Power Factor C | INT32 | 0.001 Units
41237
41239
41241
| 41243 | kWh | UINT32 | WH
| 41245 | kVAh | UINT32 | VA
41247
| 41249 | Frequency | UINT32 | 0.01 Hz
41251
41253
| 41255 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 41257 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
41259
| 41261 | Meter Total Watts | UINT32 | 0.01 W
| 41263 | Meter Total VA | UINT32 | 0.01 VA
41265
| Meter x Information |  | where x = 1 ... 43
| Meter Id | Start Address
| 1 | 41100
| 2 | 41200
| 3 | 41300
| 4 | 41400
| 5 | 41500
| 6 | 41600
| 7 | 41700
| 8 | 41800
| 9 | 41900
| 10 | 42000
| 11 | 42100
| 12 | 42200
| 13 | 42300
| 14 | 42400
| 15 | 42500
| 16 | 42600
| 17 | 42700
| 18 | 42800
| 19 | 42900
| 20 | 43000
| 21 | 43100
| 22 | 43200
| 23 | 43300
| 24 | 43400
| 25 | 43500
| 26 | 43600
| 27 | 43700
| 28 | 43800
| 29 | 43900
| 30 | 44000
| 31 | 44100
| 32 | 44200
| 33 | 44300
| 34 | 44400
| 35 | 44500
| 36 | 44600
| 37 | 44700
| 38 | 44800
| 39 | 44900
| 40 | 45000
| 41 | 45100
| 42 | 45200
| 43 | 45300
The start address for the meter is listed in the table above
| Modbus Address | Name | Format | Unit | Default | Description/Format
| 41x00 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 41x01 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41x03 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41x05 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 41x07 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41x09 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41x11 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 41x13 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41x15 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41x17 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41x19 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41x21 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 41x23 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
41x25
41x27
41x29
| 41x31 | Power Factor A | INT32 | 0.001 Units
| 41x33 | Power Factor B | INT32 | 0.001 Units
| 41x35 | Power Factor C | INT32 | 0.001 Units
41x37
41x39
| 41x41 | [5 empty] | `
| 41x43 | kWh | UINT32 | Wh
| 41x45 | kVAh | UINT32 | VAh
41x47
| 41x49 | Frequency | UINT32 | 0.01 Hz
| 41x51 |  | INT32 | W
| 41x53 |  | INT32 | W
| 41x55 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 41x57 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
41x59
| 41x61 | Meter Total Watts | UINT32 | 0.01 W
| 41x63 | Meter Total VA | UINT32 | 0.01 VA
| 41x65 |  | INT32 | W |  | Sets the kW threshold that sets the demand flag.
Mini Register Map
| Modbus Address | Name | Format | Unit | Default | Description/Format
Meter 1 | 48000 | kWh | UINT32 | Wh
48002
48004
| 48006 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48008 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 2 | 48010 | kWh | UINT32 | Wh
48012
48014
| 48016 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48018 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 3 | 48020 | kWh | UINT32 | Wh
48022
48024
| 48026 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48028 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 4 | 48030 | kWh | UINT32 | Wh
48032
48034
| 48036 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48038 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 5 | 48040 | kWh | UINT32 | Wh
48042
48044
| 48046 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48048 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 6 | 48050 | kWh | UINT32 | Wh
48052
48054
| 48056 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48058 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 7 | 48060 | kWh | UINT32 | Wh
48062
48064
| 48066 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48068 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 8 | 48070 | kWh | UINT32 | Wh
48072
48074
| 48076 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48078 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 9 | 48080 | kWh | UINT32 | Wh
48082
48084
| 48086 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48088 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 10 | 48090 | kWh | UINT32 | Wh
48092
48094
| 48096 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48098 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 11 | 48100 | kWh | UINT32 | Wh
48102
48104
| 48106 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48108 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 12 | 48110 | kWh | UINT32 | Wh
48112
48114
| 48116 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48118 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 13 | 48120 | kWh | UINT32 | Wh
48122
48124
| 48126 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48128 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 14 | 48130 | kWh | UINT32 | Wh
48132
48134
| 48136 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48138 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 15 | 48140 | kWh | UINT32 | Wh
48142
48144
| 48146 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48148 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 16 | 48150 | kWh | UINT32 | Wh
48152
48154
| 48156 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48158 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 17 | 48160 | kWh | UINT32 | Wh
48162
48164
| 48166 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48168 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 18 | 48170 | kWh | UINT32 | Wh
48172
48174
| 48176 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48178 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 19 | 48180 | kWh | UINT32 | Wh
48182
48184
| 48186 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48188 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 20 | 48190 | kWh | UINT32 | Wh
48192
48194
| 48196 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48198 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 21 | 48200 | kWh | UINT32 | Wh
48202
48204
| 48206 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48208 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 22 | 48210 | kWh | UINT32 | Wh
48212
48214
| 48216 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48218 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 23 | 48220 | kWh | UINT32 | Wh
48222
48224
| 48226 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48228 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 24 | 48230 | kWh | UINT32 | Wh
48232
48234
| 48236 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48238 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 25 | 48240 | kWh | UINT32 | Wh
48242
48244
| 48246 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48248 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 26 | 48250 | kWh | UINT32 | Wh
48252
48254
| 48256 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48258 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 27 | 48260 | kWh | UINT32 | Wh
48262
48264
| 48266 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48268 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 28 | 48270 | kWh | UINT32 | Wh
48272
48274
| 48276 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48278 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 29 | 48280 | kWh | UINT32 | Wh
48282
48284
| 48286 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48288 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 30 | 48290 | kWh | UINT32 | Wh
48292
48294
| 48296 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48298 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 31 | 48300 | kWh | UINT32 | Wh
48302
48304
| 48306 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48308 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 32 | 48310 | kWh | UINT32 | Wh
48312
48314
| 48316 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48318 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 33 | 48320 | kWh | UINT32 | Wh
48322
48324
| 48326 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48328 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 34 | 48330 | kWh | UINT32 | Wh
48332
48334
| 48336 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48338 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 35 | 48340 | kWh | UINT32 | Wh
48342
48344
| 48346 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48348 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 36 | 48350 | kWh | UINT32 | Wh
48352
48354
| 48356 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48358 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 37 | 48360 | kWh | UINT32 | Wh
48362
48364
| 48366 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48368 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 38 | 48370 | kWh | UINT32 | Wh
48372
48374
| 48376 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48378 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 39 | 48380 | kWh | UINT32 | Wh
48382
48384
| 48386 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48388 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 40 | 48390 | kWh | UINT32 | Wh
48392
48394
| 48396 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48398 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 41 | 48400 | kWh | UINT32 | Wh
48402
48404
| 48406 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48408 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 42 | 48410 | kWh | UINT32 | Wh
48412
48414
| 48416 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48418 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 43 | 48420 | kWh | UINT32 | Wh
48422
48424
| 48426 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48428 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Element 0 | 47000 | Meter | Enum |  |  | The meter that this element is associated with
| 47001 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47002 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47003 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47004 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47005 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47006 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47007 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47008 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47009 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47010 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47011 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47012 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 1 | 47020 | Meter | Enum |  |  | The meter that this element is associated with
| 47021 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47022 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47023 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47024 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47025 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47026 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47027 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47028 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47029 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47030 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47031 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47032 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 2 | 47040 | Meter | Enum |  |  | The meter that this element is associated with
| 47041 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47042 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47043 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47044 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47045 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47046 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47047 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47048 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47049 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47050 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47051 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47052 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 3 | 47060 | Meter | Enum |  |  | The meter that this element is associated with
| 47061 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47062 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47063 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47064 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47065 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47066 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47067 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47068 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47069 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47070 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47071 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47072 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 4 | 47080 | Meter | Enum |  |  | The meter that this element is associated with
| 47081 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47082 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47083 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47084 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47085 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47086 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47087 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47088 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47089 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47090 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47091 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47092 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 5 | 47100 | Meter | Enum |  |  | The meter that this element is associated with
| 47101 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47102 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47103 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47104 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47105 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47106 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47107 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47108 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47109 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47110 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47111 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47112 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 6 | 47120 | Meter | Enum |  |  | The meter that this element is associated with
| 47121 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47122 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47123 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47124 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47125 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47126 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47127 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47128 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47129 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47130 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47131 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47132 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 7 | 47140 | Meter | Enum |  |  | The meter that this element is associated with
| 47141 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47142 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47143 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47144 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47145 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47146 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47147 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47148 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47149 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47150 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47151 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47152 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 8 | 47160 | Meter | Enum |  |  | The meter that this element is associated with
| 47161 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47162 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47163 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47164 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47165 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47166 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47167 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47168 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47169 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47170 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47171 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47172 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 9 | 47180 | Meter | Enum |  |  | The meter that this element is associated with
| 47181 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47182 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47183 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47184 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47185 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47186 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47187 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47188 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47189 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47190 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47191 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47192 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 10 | 47200 | Meter | Enum |  |  | The meter that this element is associated with
| 47201 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47202 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47203 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47204 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47205 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47206 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47207 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47208 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47209 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47210 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47211 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47212 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 11 | 47220 | Meter | Enum |  |  | The meter that this element is associated with
| 47221 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47222 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47223 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47224 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47225 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47226 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47227 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47228 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47229 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47230 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47231 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47232 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 12 | 47240 | Meter | Enum |  |  | The meter that this element is associated with
| 47241 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47242 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47243 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47244 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47245 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47246 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47247 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47248 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47249 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47250 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47251 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47252 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 13 | 47260 | Meter | Enum |  |  | The meter that this element is associated with
| 47261 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47262 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47263 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47264 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47265 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47266 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47267 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47268 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47269 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47270 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47271 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47272 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 14 | 47280 | Meter | Enum |  |  | The meter that this element is associated with
| 47281 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47282 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47283 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47284 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47285 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47286 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47287 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47288 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47289 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47290 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47291 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47292 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 15 | 47300 | Meter | Enum |  |  | The meter that this element is associated with
| 47301 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47302 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47303 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47304 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47305 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47306 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47307 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47308 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47309 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47310 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47311 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47312 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 16 | 47320 | Meter | Enum |  |  | The meter that this element is associated with
| 47321 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47322 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47323 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47324 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47325 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47326 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47327 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47328 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47329 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47330 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47331 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47332 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 17 | 47340 | Meter | Enum |  |  | The meter that this element is associated with
| 47341 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47342 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47343 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47344 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47345 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47346 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47347 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47348 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47349 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47350 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47351 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47352 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 18 | 47360 | Meter | Enum |  |  | The meter that this element is associated with
| 47361 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47362 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47363 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47364 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47365 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47366 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47367 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47368 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47369 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47370 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47371 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47372 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 19 | 47380 | Meter | Enum |  |  | The meter that this element is associated with
| 47381 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47382 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47383 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47384 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47385 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47386 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47387 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47388 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47389 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47390 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47391 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47392 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 20 | 47400 | Meter | Enum |  |  | The meter that this element is associated with
| 47401 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47402 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47403 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47404 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47405 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47406 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47407 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47408 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47409 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47410 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47411 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47412 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 21 | 47420 | Meter | Enum |  |  | The meter that this element is associated with
| 47421 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47422 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47423 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47424 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47425 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47426 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47427 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47428 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47429 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47430 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47431 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47432 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 22 | 47440 | Meter | Enum |  |  | The meter that this element is associated with
| 47441 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47442 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47443 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47444 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47445 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47446 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47447 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47448 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47449 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47450 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47451 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47452 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 23 | 47460 | Meter | Enum |  |  | The meter that this element is associated with
| 47461 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47462 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47463 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47464 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47465 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47466 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47467 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47468 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47469 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47470 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47471 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47472 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 24 | 47480 | Meter | Enum |  |  | The meter that this element is associated with
| 47481 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47482 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47483 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47484 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47485 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47486 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47487 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47488 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47489 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47490 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47491 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47492 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 25 | 47500 | Meter | Enum |  |  | The meter that this element is associated with
| 47501 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47502 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47503 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47504 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47505 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47506 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47507 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47508 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47509 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47510 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47511 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47512 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 26 | 47520 | Meter | Enum |  |  | The meter that this element is associated with
| 47521 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47522 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47523 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47524 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47525 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47526 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47527 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47528 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47529 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47530 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47531 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47532 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 27 | 47540 | Meter | Enum |  |  | The meter that this element is associated with
| 47541 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47542 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47543 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47544 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47545 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47546 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47547 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47548 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47549 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47550 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47551 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47552 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 28 | 47560 | Meter | Enum |  |  | The meter that this element is associated with
| 47561 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47562 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47563 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47564 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47565 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47566 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47567 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47568 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47569 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47570 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47571 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47572 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 29 | 47580 | Meter | Enum |  |  | The meter that this element is associated with
| 47581 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47582 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47583 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47584 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47585 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47586 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47587 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47588 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47589 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47590 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47591 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47592 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 30 | 47600 | Meter | Enum |  |  | The meter that this element is associated with
| 47601 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47602 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47603 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47604 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47605 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47606 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47607 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47608 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47609 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47610 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47611 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47612 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 31 | 47620 | Meter | Enum |  |  | The meter that this element is associated with
| 47621 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47622 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47623 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47624 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47625 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47626 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47627 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47628 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47629 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47630 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47631 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47632 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 32 | 47640 | Meter | Enum |  |  | The meter that this element is associated with
| 47641 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47642 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47643 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47644 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47645 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47646 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47647 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47648 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47649 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47650 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47651 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47652 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 33 | 47660 | Meter | Enum |  |  | The meter that this element is associated with
| 47661 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47662 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47663 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47664 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47665 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47666 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47667 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47668 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47669 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47670 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47671 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47672 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 34 | 47680 | Meter | Enum |  |  | The meter that this element is associated with
| 47681 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47682 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47683 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47684 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47685 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47686 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47687 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47688 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47689 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47690 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47691 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47692 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 35 | 47700 | Meter | Enum |  |  | The meter that this element is associated with
| 47701 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47702 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47703 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47704 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47705 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47706 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47707 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47708 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47709 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47710 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47711 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47712 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 36 | 47720 | Meter | Enum |  |  | The meter that this element is associated with
| 47721 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47722 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47723 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47724 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47725 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47726 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47727 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47728 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47729 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47730 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47731 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47732 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 37 | 47740 | Meter | Enum |  |  | The meter that this element is associated with
| 47741 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47742 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47743 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47744 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47745 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47746 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47747 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47748 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47749 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47750 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47751 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47752 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 38 | 47760 | Meter | Enum |  |  | The meter that this element is associated with
| 47761 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47762 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47763 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47764 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47765 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47766 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47767 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47768 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47769 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47770 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47771 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47772 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 39 | 47780 | Meter | Enum |  |  | The meter that this element is associated with
| 47781 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47782 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47783 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47784 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47785 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47786 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47787 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47788 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47789 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47790 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47791 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47792 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 40 | 47800 | Meter | Enum |  |  | The meter that this element is associated with
| 47801 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47802 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47803 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47804 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47805 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47806 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47807 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47808 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47809 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47810 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47811 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47812 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 41 | 47820 | Meter | Enum |  |  | The meter that this element is associated with
| 47821 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47822 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47823 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47824 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47825 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47826 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47827 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47828 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47829 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47830 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47831 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47832 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 42 | 47840 | Meter | Enum |  |  | The meter that this element is associated with
| 47841 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47842 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47843 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47844 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47845 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47846 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47847 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47848 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47849 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47850 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47851 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47852 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 43 | 47860 | Meter | Enum |  |  | The meter that this element is associated with
| 47861 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47862 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47863 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47864 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47865 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47866 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47867 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47868 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47869 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47870 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47871 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47872 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 44 | 47880 | Meter | Enum |  |  | The meter that this element is associated with
| 47881 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47882 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47883 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47884 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47885 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47886 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47887 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47888 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47889 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47890 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47891 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47892 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage A | 47900 | Meter | Bit Field |  |  | The corresponding meter bit is set for each meter that is associated with this voltage
| 47901 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47902 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47903 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47904 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47905 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47906 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47907 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47908 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47909 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47910 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47911 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47912 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage B | 47920 | Meter | Bit Field |  |  | The corresponding meter bit is set for each meter that is associated with this voltage
| 47921 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47922 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47923 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47924 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47925 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47926 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47927 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47928 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47929 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47930 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47931 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47932 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage C | 47940 | Meter | Bit Field |  |  | The corresponding meter bit is set for each meter that is associated with this voltage
| 47941 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47942 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47943 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47944 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47945 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47946 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47947 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47948 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47949 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47950 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47951 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47952 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform

## i-636_V3.55
System Parameters - Read Only
| Modbus Address | Name | Format | Scale | Default | Description/Format
| 40001 | Serial Number Low | UINT16 | x1 |  | This is consistent with the original document. This is effectively little Endian UINT32
| 40002 | Serial Number High | UINT16 | x1 |  | This is consistent with the original document. This is effectively little Endian UINT32
| 40003 | Firmware Version | UINT16 | x1
| 40004 | OEM Identification | UINT16 | x1 |  | "PT" in ASCII
| 40005 | Meter Model | UINT16 | x1 | 636 | {109, 431, 636,45, 888}
| 40014 | Number of Curent Element on Unit | UINT16 | x1 | 16 | This is a maximum of 16 on the MP636
| 40015 | Number of Meters on Unit | UINT16 | x1 |  | For the MP636, this will be 6, 8, or 16, for the 5x3 phase (+1x1phase), 8x2phase, or 16x1 phase
| 40016 | Modbus Uptime | UINT32 | x1 |  | This is the number of seconds since the last power cycle on the modbus module.
| 40019 | Meter Config | UINT16 | x1 |  | The configuration of the meter
Configuration Parameters
| Modbus Address | Name | Format | Access | Default | Description/Format
48000-7000 | 48000 | PTRatio | UINT16 | R/W | 1 | The PT ratio that will be used in calculations. It does not affect meter operation.
48001
| 48002 | Address | UINT16 | R/W | 1 | Changes to the Modbus address take effect immediately. The next command must use the changed address, otherwise the module will not respond
| 48003 | Baud Rate | Enumated | R/W | 3 = 9600 bps | 3 = 9600 bps 4 = 19200 bps 5 = 38400 bps 6 = 57600 bps 7 = 115200 bps
| 48004 | CT Ratio - Meter 1 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48005 | CT Ratio - Meter 2 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48006 | CT Ratio - Meter 3 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48007 | CT Ratio - Meter 4 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48008 | CT Ratio - Meter 5 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48009 | CT Ratio - Meter 6 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48010 | CT Ratio - Meter 7 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48011 | CT Ratio - Meter 8 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48012 | CT Ratio - Meter 9 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48013 | CT Ratio - Meter 10 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48014 | CT Ratio - Meter 11 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48015 | CT Ratio - Meter 12 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48016 | CT Ratio - Meter 13 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48017 | CT Ratio - Meter 14 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48018 | CT Ratio - Meter 15 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48019 | CT Ratio - Meter 16 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48020 | Demand Intervals | Enumerated | R/W | 2 | 0 = 1 minute 1 = 5 minutes 2 = 15 minutes 3 = 30 minutes 4 = 60 minutes 5 = Disabled
| 48050 | CT Ratio - Meter 1 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48051 | CT Ratio - Meter 2 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48052 | CT Ratio - Meter 3 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48053 | CT Ratio - Meter 4 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48054 | CT Ratio - Meter 5 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48055 | CT Ratio - Meter 6 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48056 | CT Ratio - Meter 7 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48057 | CT Ratio - Meter 8 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48058 | CT Ratio - Meter 9 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48059 | CT Ratio - Meter 10 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48060 | CT Ratio - Meter 11 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48061 | CT Ratio - Meter 12 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48062 | CT Ratio - Meter 13 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48063 | CT Ratio - Meter 14 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48064 | CT Ratio - Meter 15 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48065 | CT Ratio - Meter 16 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48066 | CT Ratio - Meter 17 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48067 | CT Ratio - Meter 18 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48068 | CT Ratio - Meter 19 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48069 | CT Ratio - Meter 20 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48070 | CT Ratio - Meter 21 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48071 | CT Ratio - Meter 22 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48072 | CT Ratio - Meter 23 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48073 | CT Ratio - Meter 24 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48074 | CT Ratio - Meter 25 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48075 | CT Ratio - Meter 26 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48076 | CT Ratio - Meter 27 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48077 | CT Ratio - Meter 28 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48078 | CT Ratio - Meter 29 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48079 | CT Ratio - Meter 30 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48080 | CT Ratio - Meter 31 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48081 | CT Ratio - Meter 32 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48082 | CT Ratio - Meter 33 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48083 | CT Ratio - Meter 34 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48084 | CT Ratio - Meter 35 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48085 | CT Ratio - Meter 36 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48086 | CT Ratio - Meter 37 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48087 | CT Ratio - Meter 38 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48088 | CT Ratio - Meter 39 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48089 | CT Ratio - Meter 40 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48090 | CT Ratio - Meter 41 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48091 | CT Ratio - Meter 42 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
| 48092 | CT Ratio - Meter 43 | UINT16 | R/W | 2000 | The CT ratio that will be used in calculations. Minimum value of 1000.
Meter 1 Information
| Modbus Address | Name | Format | Unit | Default | Description/Format
-7000 | 48100 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 48101 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48103 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48105 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48107 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48109 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48111 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48113 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48115 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48117 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48119 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48121 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48123 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
48125
48127
48129
| 48131 | Power Factor A | INT32 | 0.001 Units
| 48133 | Power Factor B | INT32 | 0.001 Units
| 48135 | Power Factor C | INT32 | 0.001 Units
48137
48139
48141
| 48143 | kWh | UINT32 | Wh
| 48145 | kVAh | UINT32 | VAh
48147
| 48149 | Frequency | UINT32 | 0.01 Hz
| 48151 | Meter Demand Average | INT32 | W
| 48153 | Meter Demand Peak | INT32 | W
| 48155 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48157 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
48159
| 48161 | Meter Total Watts | UINT32 | 0.01 W
| 48163 | Meter Total VA | UINT32 | 0.01 VA
48165
48167
48169
Meter 2 Information
| Modbus Address | Name | Format | Unit | Default | Description/Format
| 48200 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 48201 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48203 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48205 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48207 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48209 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48211 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48213 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48215 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48217 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48219 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48221 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48223 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
48225
48227
48229
| 48231 | Power Factor A | INT32 | 0.001 Units
| 48233 | Power Factor B | INT32 | 0.001 Units
| 48235 | Power Factor C | INT32 | 0.001 Units
48237
48239
48241
| 48243 | kWh | UINT32 | WH
| 48245 | kVAh | UINT32 | VA
48247
| 48249 | Frequency | UINT32 | 0.01 Hz
| 48251 | Watt Demand Average | INT32 | W
| 48253 | Watt Demand Peak | INT32 | W
| 48255 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48257 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
48259
| 48261 | Meter Total Watts | UINT32 | 0.01 W
| 48263 | Meter Total VA | UINT32 | 0.01 VA
48265
| Meter x Information |  | where x = 1 ... 43
| Meter Id | Start Address
| 1 | 41100
| 2 | 48200
| 3 | 48300
| 4 | 48400
| 5 | 48500
| 6 | 48600
| 7 | 48700
| 8 | 48800
| 9 | 48900
| 10 | 49000
| 11 | 49100
| 12 | 49200
| 13 | 49300
| 14 | 49400
| 15 | 49500
| 16 | 49600
| 17 | 49700
| 18 | 49800
| 19 | 49900
| 20 | 50000
| 21 | 50100
| 22 | 50200
| 23 | 50300
| 24 | 50400
| 25 | 50500
| 26 | 50600
| 27 | 50700
| 28 | 50800
| 29 | 50900
| 30 | 51000
| 31 | 51100
| 32 | 51200
| 33 | 51300
| 34 | 51400
| 35 | 51500
| 36 | 51600
| 37 | 51700
| 38 | 51800
| 39 | 51900
| 40 | 52000
| 41 | 52100
| 42 | 52200
| 43 | 52300
The start address for the meter is listed in the table above
| Modbus Address | Name | Format | Unit | Default | Description/Format
| 48x00 | Acitve Phases | Bit map | x1 |  | 0x0001 - Meter uses phase A 0x0002 - Meter uses phase B 0x0004 - Meter uses phase C
| 48x01 | Voltage A | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48x03 | Voltage B | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48x05 | Voltage C | UINT32 | mV |  | The value will be the reported voltage * PT Ratio
| 48x07 | Current A | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48x09 | Current B | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48x11 | Current C | UINT32 | mA |  | The value will be the reported current * CTRatio/5
| 48x13 | Watts A | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48x15 | Watts B | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48x17 | Watts C | INT32 | 0.01 W |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48x19 | Volt-Amp A | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48x21 | Volt-Amp B | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
| 48x23 | Volt-Amp C | INT32 | 0.01 VA |  | The value will be the reported power * PT Ratio * CT Ratio / 5
48x25
48x27
48x29
| 48x31 | Power Factor A | INT32 | 0.001 Units
| 48x33 | Power Factor B | INT32 | 0.001 Units
| 48x35 | Power Factor C | INT32 | 0.001 Units
48x37
48x39
| 48x41 | [5 empty] | `
| 48x43 | kWh | UINT32 | Wh
| 48x45 | kVAh | UINT32 | VAh
48x47
| 48x49 | Frequency | UINT32 | 0.01 Hz
| 48x51 | Watt Demand Average | INT32 | W
| 48x53 | Watt Demand Peak | INT32 | W
| 48x55 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 48x57 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
48x59
| 48x61 | Meter Total Watts | UINT32 | 0.01 W
| 48x63 | Meter Total VA | UINT32 | 0.01 VA
| 48x65 | kW Demand exceeds set value | INT32 | W |  | Sets the kW threshold that sets the demand flag.
Mini Register Map
| Modbus Address | Name | Format | Unit | Default | Description/Format
Meter 1 | 53000 | kWh | UINT32 | Wh
48000 | 53002 | Demand Average | UINT32 | W
| 53004 | Demand Peak | UINT32 | W
| 53006 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53008 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 2 | 53010 | kWh | UINT32 | Wh
| 53012 | Demand Average | UINT32 | W
| 53014 | Demand Peak | UINT32 | W
| 53016 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53018 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 3 | 53020 | kWh | UINT32 | Wh
| 53022 | Demand Average | UINT32 | W
| 53024 | Demand Peak | UINT32 | W
| 53026 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53028 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 4 | 53030 | kWh | UINT32 | Wh
| 53032 | Demand Average | UINT32 | W
| 53034 | Demand Peak | UINT32 | W
| 53036 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53038 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 5 | 53040 | kWh | UINT32 | Wh
| 53042 | Demand Average | UINT32 | W
| 53044 | Demand Peak | UINT32 | W
| 53046 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53048 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 6 | 53050 | kWh | UINT32 | Wh
| 53052 | Demand Average | UINT32 | W
| 53054 | Demand Peak | UINT32 | W
| 53056 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53058 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 7 | 53060 | kWh | UINT32 | Wh
| 53062 | Demand Average | UINT32 | W
| 53064 | Demand Peak | UINT32 | W
| 53066 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53068 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 8 | 53070 | kWh | UINT32 | Wh
| 53072 | Demand Average | UINT32 | W
| 53074 | Demand Peak | UINT32 | W
| 53076 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53078 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 9 | 53080 | kWh | UINT32 | Wh
| 53082 | Demand Average | UINT32 | W
| 53084 | Demand Peak | UINT32 | W
| 53086 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53088 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 10 | 53090 | kWh | UINT32 | Wh
| 53092 | Demand Average | UINT32 | W
| 53094 | Demand Peak | UINT32 | W
| 53096 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53098 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 11 | 53100 | kWh | UINT32 | Wh
| 53102 | Demand Average | UINT32 | W
| 53104 | Demand Peak | UINT32 | W
| 53106 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53108 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 12 | 53110 | kWh | UINT32 | Wh
| 53112 | Demand Average | UINT32 | W
| 53114 | Demand Peak | UINT32 | W
| 53116 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53118 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 13 | 53120 | kWh | UINT32 | Wh
| 53122 | Demand Average | UINT32 | W
| 53124 | Demand Peak | UINT32 | W
| 53126 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53128 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 14 | 53130 | kWh | UINT32 | Wh
| 53132 | Demand Average | UINT32 | W
| 53134 | Demand Peak | UINT32 | W
| 53136 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53138 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 15 | 53140 | kWh | UINT32 | Wh
| 53142 | Demand Average | UINT32 | W
| 53144 | Demand Peak | UINT32 | W
| 53146 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53148 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 16 | 53150 | kWh | UINT32 | Wh
| 53152 | Demand Average | UINT32 | W
| 53154 | Demand Peak | UINT32 | W
| 53156 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53158 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 17 | 53160 | kWh | UINT32 | Wh
| 53162 | Demand Average | UINT32 | W
| 53164 | Demand Peak | UINT32 | W
| 53166 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53168 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 18 | 53170 | kWh | UINT32 | Wh
| 53172 | Demand Average | UINT32 | W
| 53174 | Demand Peak | UINT32 | W
| 53176 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53178 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 19 | 53180 | kWh | UINT32 | Wh
| 53182 | Demand Average | UINT32 | W
| 53184 | Demand Peak | UINT32 | W
| 53186 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53188 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 20 | 53190 | kWh | UINT32 | Wh
| 53192 | Demand Average | UINT32 | W
| 53194 | Demand Peak | UINT32 | W
| 53196 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53198 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 21 | 53200 | kWh | UINT32 | Wh
| 53202 | Demand Average | UINT32 | W
| 53204 | Demand Peak | UINT32 | W
| 53206 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53208 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 22 | 53210 | kWh | UINT32 | Wh
| 53212 | Demand Average | UINT32 | W
| 53214 | Demand Peak | UINT32 | W
| 53216 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53218 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 23 | 53220 | kWh | UINT32 | Wh
| 53222 | Demand Average | UINT32 | W
| 53224 | Demand Peak | UINT32 | W
| 53226 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53228 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 24 | 53230 | kWh | UINT32 | Wh
| 53232 | Demand Average | UINT32 | W
| 53234 | Demand Peak | UINT32 | W
| 53236 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53238 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 25 | 53240 | kWh | UINT32 | Wh
| 53242 | Demand Average | UINT32 | W
| 53244 | Demand Peak | UINT32 | W
| 53246 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53248 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 26 | 53250 | kWh | UINT32 | Wh
| 53252 | Demand Average | UINT32 | W
| 53254 | Demand Peak | UINT32 | W
| 53256 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53258 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 27 | 53260 | kWh | UINT32 | Wh
| 53262 | Demand Average | UINT32 | W
| 53264 | Demand Peak | UINT32 | W
| 53266 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53268 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 28 | 53270 | kWh | UINT32 | Wh
| 53272 | Demand Average | UINT32 | W
| 53274 | Demand Peak | UINT32 | W
| 53276 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53278 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 29 | 53280 | kWh | UINT32 | Wh
| 53282 | Demand Average | UINT32 | W
| 53284 | Demand Peak | UINT32 | W
| 53286 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53288 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 30 | 53290 | kWh | UINT32 | Wh
| 53292 | Demand Average | UINT32 | W
| 53294 | Demand Peak | UINT32 | W
| 53296 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53298 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 31 | 53300 | kWh | UINT32 | Wh
| 53302 | Demand Average | UINT32 | W
| 53304 | Demand Peak | UINT32 | W
| 53306 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53308 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 32 | 53310 | kWh | UINT32 | Wh
| 53312 | Demand Average | UINT32 | W
| 53314 | Demand Peak | UINT32 | W
| 53316 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53318 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 33 | 53320 | kWh | UINT32 | Wh
| 53322 | Demand Average | UINT32 | W
| 53324 | Demand Peak | UINT32 | W
| 53326 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53328 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 34 | 53330 | kWh | UINT32 | Wh
| 53332 | Demand Average | UINT32 | W
| 53334 | Demand Peak | UINT32 | W
| 53336 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53338 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 35 | 53340 | kWh | UINT32 | Wh
| 53342 | Demand Average | UINT32 | W
| 53344 | Demand Peak | UINT32 | W
| 53346 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53348 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 36 | 53350 | kWh | UINT32 | Wh
| 53352 | Demand Average | UINT32 | W
| 53354 | Demand Peak | UINT32 | W
| 53356 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53358 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 37 | 53360 | kWh | UINT32 | Wh
| 53362 | Demand Average | UINT32 | W
| 53364 | Demand Peak | UINT32 | W
| 53366 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53368 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 38 | 53370 | kWh | UINT32 | Wh
| 53372 | Demand Average | UINT32 | W
| 53374 | Demand Peak | UINT32 | W
| 53376 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53378 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 39 | 53380 | kWh | UINT32 | Wh
| 53382 | Demand Average | UINT32 | W
| 53384 | Demand Peak | UINT32 | W
| 53386 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53388 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 40 | 53390 | kWh | UINT32 | Wh
| 53392 | Demand Average | UINT32 | W
| 53394 | Demand Peak | UINT32 | W
| 53396 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53398 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 41 | 53400 | kWh | UINT32 | Wh
| 53402 | Demand Average | UINT32 | W
| 53404 | Demand Peak | UINT32 | W
| 53406 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53408 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 42 | 53410 | kWh | UINT32 | Wh
| 53412 | Demand Average | UINT32 | W
| 53414 | Demand Peak | UINT32 | W
| 53416 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53418 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Meter 43 | 53420 | kWh | UINT32 | Wh
| 53422 | Demand Average | UINT32 | W
| 53424 | Demand Peak | UINT32 | W
| 53426 | Voltage Average | UINT32 | mV |  | Average of the voltage from each phase
| 53428 | Meter Total Current | UINT32 | mA |  | Average of the current from each phase
Element 0 | 47000 | Meter | Enum |  |  | The meter that this element is associated with
| 47001 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47002 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47003 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47004 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47005 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47006 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47007 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47008 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47009 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47010 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47011 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47012 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47013 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 1 | 47020 | Meter | Enum |  |  | The meter that this element is associated with
| 47021 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47022 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47023 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47024 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47025 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47026 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47027 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47028 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47029 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47030 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47031 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47032 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47033 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 2 | 47040 | Meter | Enum |  |  | The meter that this element is associated with
| 47041 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47042 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47043 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47044 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47045 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47046 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47047 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47048 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47049 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47050 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47051 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47052 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47053 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 3 | 47060 | Meter | Enum |  |  | The meter that this element is associated with
| 47061 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47062 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47063 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47064 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47065 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47066 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47067 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47068 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47069 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47070 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47071 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47072 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47073 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 4 | 47080 | Meter | Enum |  |  | The meter that this element is associated with
| 47081 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47082 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47083 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47084 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47085 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47086 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47087 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47088 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47089 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47090 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47091 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47092 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47093 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 5 | 47100 | Meter | Enum |  |  | The meter that this element is associated with
| 47101 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47102 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47103 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47104 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47105 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47106 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47107 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47108 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47109 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47110 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47111 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47112 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47113 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 6 | 47120 | Meter | Enum |  |  | The meter that this element is associated with
| 47121 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47122 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47123 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47124 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47125 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47126 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47127 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47128 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47129 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47130 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47131 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47132 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47133 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 7 | 47140 | Meter | Enum |  |  | The meter that this element is associated with
| 47141 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47142 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47143 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47144 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47145 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47146 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47147 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47148 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47149 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47150 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47151 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47152 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47153 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 8 | 47160 | Meter | Enum |  |  | The meter that this element is associated with
| 47161 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47162 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47163 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47164 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47165 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47166 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47167 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47168 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47169 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47170 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47171 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47172 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47173 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 9 | 47180 | Meter | Enum |  |  | The meter that this element is associated with
| 47181 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47182 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47183 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47184 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47185 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47186 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47187 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47188 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47189 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47190 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47191 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47192 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47193 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 10 | 47200 | Meter | Enum |  |  | The meter that this element is associated with
| 47201 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47202 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47203 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47204 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47205 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47206 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47207 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47208 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47209 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47210 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47211 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47212 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47213 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 11 | 47220 | Meter | Enum |  |  | The meter that this element is associated with
| 47221 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47222 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47223 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47224 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47225 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47226 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47227 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47228 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47229 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47230 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47231 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47232 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47233 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 12 | 47240 | Meter | Enum |  |  | The meter that this element is associated with
| 47241 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47242 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47243 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47244 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47245 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47246 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47247 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47248 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47249 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47250 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47251 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47252 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47253 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 13 | 47260 | Meter | Enum |  |  | The meter that this element is associated with
| 47261 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47262 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47263 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47264 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47265 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47266 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47267 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47268 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47269 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47270 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47271 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47272 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47273 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 14 | 47280 | Meter | Enum |  |  | The meter that this element is associated with
| 47281 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47282 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47283 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47284 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47285 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47286 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47287 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47288 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47289 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47290 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47291 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47292 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47293 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 15 | 47300 | Meter | Enum |  |  | The meter that this element is associated with
| 47301 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47302 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47303 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47304 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47305 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47306 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47307 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47308 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47309 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47310 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47311 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47312 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47313 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 16 | 47300 | Meter | Enum |  |  | The meter that this element is associated with
| 47301 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47302 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47303 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47304 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47305 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47306 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47307 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47308 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47309 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47310 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47311 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47312 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47313 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 17 | 47320 | Meter | Enum |  |  | The meter that this element is associated with
| 47321 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47322 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47323 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47324 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47325 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47326 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47327 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47328 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47329 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47330 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47331 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47332 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47333 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 18 | 47340 | Meter | Enum |  |  | The meter that this element is associated with
| 47341 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47342 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47343 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47344 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47345 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47346 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47347 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47348 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47349 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47350 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47351 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47352 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47353 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 19 | 47360 | Meter | Enum |  |  | The meter that this element is associated with
| 47361 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47362 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47363 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47364 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47365 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47366 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47367 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47368 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47369 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47370 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47371 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47372 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47373 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 20 | 47380 | Meter | Enum |  |  | The meter that this element is associated with
| 47381 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47382 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47383 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47384 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47385 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47386 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47387 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47388 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47389 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47390 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47391 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47392 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47393 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 21 | 47400 | Meter | Enum |  |  | The meter that this element is associated with
| 47401 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47402 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47403 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47404 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47405 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47406 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47407 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47408 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47409 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47410 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47411 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47412 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47413 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 22 | 47420 | Meter | Enum |  |  | The meter that this element is associated with
| 47421 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47422 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47423 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47424 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47425 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47426 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47427 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47428 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47429 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47430 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47431 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47432 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47433 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 23 | 47440 | Meter | Enum |  |  | The meter that this element is associated with
| 47441 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47442 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47443 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47444 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47445 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47446 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47447 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47448 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47449 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47450 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47451 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47452 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47453 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 24 | 47460 | Meter | Enum |  |  | The meter that this element is associated with
| 47461 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47462 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47463 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47464 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47465 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47466 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47467 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47468 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47469 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47470 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47471 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47472 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47473 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 25 | 47480 | Meter | Enum |  |  | The meter that this element is associated with
| 47481 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47482 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47483 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47484 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47485 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47486 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47487 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47488 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47489 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47490 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47491 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47492 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47493 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 26 | 47500 | Meter | Enum |  |  | The meter that this element is associated with
| 47501 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47502 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47503 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47504 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47505 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47506 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47507 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47508 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47509 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47510 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47511 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47512 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47513 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 27 | 47520 | Meter | Enum |  |  | The meter that this element is associated with
| 47521 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47522 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47523 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47524 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47525 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47526 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47527 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47528 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47529 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47530 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47531 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47532 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47533 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 28 | 47540 | Meter | Enum |  |  | The meter that this element is associated with
| 47541 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47542 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47543 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47544 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47545 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47546 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47547 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47548 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47549 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47550 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47551 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47552 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47553 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 29 | 47560 | Meter | Enum |  |  | The meter that this element is associated with
| 47561 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47562 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47563 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47564 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47565 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47566 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47567 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47568 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47569 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47570 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47571 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47572 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47573 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 30 | 47580 | Meter | Enum |  |  | The meter that this element is associated with
| 47581 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47582 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47583 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47584 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47585 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47586 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47587 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47588 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47589 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47590 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47591 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47592 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47593 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 31 | 47600 | Meter | Enum |  |  | The meter that this element is associated with
| 47601 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47602 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47603 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47604 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47605 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47606 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47607 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47608 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47609 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47610 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47611 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47612 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47613 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 32 | 47620 | Meter | Enum |  |  | The meter that this element is associated with
| 47621 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47622 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47623 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47624 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47625 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47626 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47627 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47628 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47629 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47630 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47631 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47632 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47633 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 33 | 47640 | Meter | Enum |  |  | The meter that this element is associated with
| 47641 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47642 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47643 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47644 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47645 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47646 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47647 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47648 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47649 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47650 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47651 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47652 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47653 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 34 | 47660 | Meter | Enum |  |  | The meter that this element is associated with
| 47661 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47662 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47663 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47664 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47665 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47666 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47667 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47668 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47669 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47670 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47671 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47672 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47673 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 35 | 47680 | Meter | Enum |  |  | The meter that this element is associated with
| 47681 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47682 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47683 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47684 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47685 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47686 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47687 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47688 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47689 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47690 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47691 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47692 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47693 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 36 | 47700 | Meter | Enum |  |  | The meter that this element is associated with
| 47701 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47702 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47703 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47704 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47705 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47706 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47707 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47708 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47709 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47710 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47711 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47712 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47713 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 37 | 47720 | Meter | Enum |  |  | The meter that this element is associated with
| 47721 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47722 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47723 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47724 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47725 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47726 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47727 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47728 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47729 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47730 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47731 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47732 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47733 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 38 | 47740 | Meter | Enum |  |  | The meter that this element is associated with
| 47741 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47742 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47743 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47744 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47745 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47746 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47747 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47748 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47749 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47750 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47751 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47752 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47753 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 39 | 47760 | Meter | Enum |  |  | The meter that this element is associated with
| 47761 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47762 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47763 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47764 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47765 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47766 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47767 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47768 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47769 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47770 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47771 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47772 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47773 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 40 | 47780 | Meter | Enum |  |  | The meter that this element is associated with
| 47781 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47782 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47783 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47784 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47785 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47786 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47787 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47788 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47789 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47790 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47791 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47792 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47793 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 41 | 47800 | Meter | Enum |  |  | The meter that this element is associated with
| 47801 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47802 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47803 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47804 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47805 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47806 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47807 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47808 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47809 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47810 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47811 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47812 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47813 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 42 | 47820 | Meter | Enum |  |  | The meter that this element is associated with
| 47821 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47822 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47823 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47824 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47825 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47826 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47827 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47828 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47829 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47830 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47831 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47832 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47833 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 43 | 47840 | Meter | Enum |  |  | The meter that this element is associated with
| 47841 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47842 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47843 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47844 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47845 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47846 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47847 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47848 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47849 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47850 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47851 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47852 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47853 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage A | 47860 | Meter | Enum |  |  | The meter that this element is associated with
| 47861 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47862 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47863 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47864 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47865 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47866 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47867 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47868 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47869 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47870 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47871 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47872 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47873 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage B | 47880 | Meter | Enum |  |  | The meter that this element is associated with
| 47881 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47882 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47883 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47884 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47885 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47886 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47887 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47888 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47889 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47890 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47891 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47892 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47893 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage C | 47900 | Meter | Enum |  |  | The meter that this element is associated with
| 47901 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47902 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47903 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47904 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47905 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47906 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47907 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47908 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47909 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47910 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47911 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47912 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47913 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 0 | 47000 | Meter | Enum |  |  | The meter that this element is associated with
| 47001 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47002 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47003 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47004 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47005 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47006 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47007 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47008 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47009 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47010 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47011 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47012 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47013 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 1 | 47020 | Meter | Enum |  |  | The meter that this element is associated with
| 47021 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47022 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47023 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47024 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47025 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47026 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47027 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47028 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47029 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47030 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47031 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47032 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47033 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 2 | 47040 | Meter | Enum |  |  | The meter that this element is associated with
| 47041 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47042 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47043 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47044 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47045 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47046 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47047 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47048 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47049 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47050 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47051 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47052 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47053 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 3 | 47060 | Meter | Enum |  |  | The meter that this element is associated with
| 47061 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47062 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47063 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47064 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47065 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47066 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47067 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47068 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47069 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47070 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47071 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47072 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47073 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 4 | 47080 | Meter | Enum |  |  | The meter that this element is associated with
| 47081 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47082 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47083 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47084 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47085 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47086 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47087 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47088 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47089 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47090 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47091 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47092 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47093 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 5 | 47100 | Meter | Enum |  |  | The meter that this element is associated with
| 47101 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47102 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47103 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47104 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47105 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47106 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47107 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47108 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47109 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47110 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47111 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47112 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47113 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 6 | 47120 | Meter | Enum |  |  | The meter that this element is associated with
| 47121 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47122 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47123 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47124 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47125 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47126 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47127 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47128 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47129 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47130 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47131 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47132 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47133 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 7 | 47140 | Meter | Enum |  |  | The meter that this element is associated with
| 47141 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47142 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47143 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47144 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47145 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47146 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47147 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47148 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47149 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47150 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47151 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47152 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47153 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 8 | 47160 | Meter | Enum |  |  | The meter that this element is associated with
| 47161 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47162 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47163 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47164 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47165 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47166 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47167 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47168 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47169 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47170 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47171 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47172 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47173 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 9 | 47180 | Meter | Enum |  |  | The meter that this element is associated with
| 47181 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47182 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47183 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47184 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47185 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47186 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47187 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47188 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47189 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47190 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47191 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47192 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47193 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 10 | 47200 | Meter | Enum |  |  | The meter that this element is associated with
| 47201 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47202 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47203 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47204 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47205 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47206 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47207 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47208 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47209 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47210 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47211 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47212 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47213 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 11 | 47220 | Meter | Enum |  |  | The meter that this element is associated with
| 47221 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47222 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47223 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47224 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47225 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47226 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47227 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47228 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47229 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47230 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47231 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47232 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47233 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 12 | 47240 | Meter | Enum |  |  | The meter that this element is associated with
| 47241 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47242 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47243 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47244 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47245 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47246 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47247 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47248 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47249 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47250 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47251 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47252 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47253 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 13 | 47260 | Meter | Enum |  |  | The meter that this element is associated with
| 47261 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47262 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47263 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47264 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47265 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47266 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47267 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47268 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47269 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47270 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47271 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47272 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47273 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 14 | 47280 | Meter | Enum |  |  | The meter that this element is associated with
| 47281 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47282 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47283 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47284 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47285 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47286 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47287 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47288 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47289 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47290 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47291 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47292 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47293 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 15 | 47300 | Meter | Enum |  |  | The meter that this element is associated with
| 47301 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47302 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47303 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47304 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47305 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47306 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47307 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47308 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47309 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47310 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47311 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47312 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47313 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 16 | 47300 | Meter | Enum |  |  | The meter that this element is associated with
| 47301 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47302 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47303 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47304 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47305 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47306 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47307 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47308 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47309 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47310 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47311 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47312 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47313 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 17 | 47320 | Meter | Enum |  |  | The meter that this element is associated with
| 47321 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47322 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47323 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47324 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47325 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47326 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47327 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47328 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47329 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47330 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47331 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47332 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47333 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 18 | 47340 | Meter | Enum |  |  | The meter that this element is associated with
| 47341 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47342 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47343 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47344 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47345 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47346 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47347 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47348 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47349 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47350 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47351 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47352 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47353 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 19 | 47360 | Meter | Enum |  |  | The meter that this element is associated with
| 47361 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47362 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47363 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47364 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47365 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47366 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47367 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47368 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47369 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47370 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47371 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47372 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47373 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 20 | 47380 | Meter | Enum |  |  | The meter that this element is associated with
| 47381 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47382 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47383 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47384 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47385 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47386 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47387 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47388 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47389 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47390 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47391 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47392 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47393 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 21 | 47400 | Meter | Enum |  |  | The meter that this element is associated with
| 47401 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47402 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47403 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47404 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47405 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47406 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47407 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47408 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47409 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47410 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47411 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47412 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47413 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 22 | 47420 | Meter | Enum |  |  | The meter that this element is associated with
| 47421 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47422 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47423 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47424 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47425 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47426 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47427 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47428 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47429 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47430 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47431 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47432 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47433 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 23 | 47440 | Meter | Enum |  |  | The meter that this element is associated with
| 47441 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47442 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47443 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47444 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47445 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47446 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47447 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47448 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47449 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47450 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47451 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47452 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47453 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 24 | 47460 | Meter | Enum |  |  | The meter that this element is associated with
| 47461 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47462 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47463 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47464 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47465 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47466 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47467 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47468 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47469 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47470 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47471 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47472 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47473 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 25 | 47480 | Meter | Enum |  |  | The meter that this element is associated with
| 47481 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47482 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47483 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47484 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47485 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47486 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47487 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47488 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47489 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47490 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47491 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47492 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47493 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 26 | 47500 | Meter | Enum |  |  | The meter that this element is associated with
| 47501 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47502 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47503 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47504 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47505 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47506 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47507 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47508 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47509 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47510 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47511 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47512 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47513 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 27 | 47520 | Meter | Enum |  |  | The meter that this element is associated with
| 47521 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47522 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47523 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47524 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47525 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47526 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47527 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47528 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47529 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47530 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47531 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47532 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47533 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 28 | 47540 | Meter | Enum |  |  | The meter that this element is associated with
| 47541 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47542 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47543 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47544 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47545 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47546 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47547 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47548 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47549 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47550 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47551 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47552 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47553 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 29 | 47560 | Meter | Enum |  |  | The meter that this element is associated with
| 47561 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47562 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47563 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47564 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47565 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47566 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47567 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47568 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47569 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47570 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47571 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47572 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47573 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 30 | 47580 | Meter | Enum |  |  | The meter that this element is associated with
| 47581 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47582 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47583 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47584 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47585 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47586 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47587 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47588 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47589 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47590 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47591 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47592 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47593 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 31 | 47600 | Meter | Enum |  |  | The meter that this element is associated with
| 47601 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47602 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47603 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47604 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47605 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47606 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47607 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47608 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47609 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47610 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47611 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47612 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47613 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 32 | 47620 | Meter | Enum |  |  | The meter that this element is associated with
| 47621 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47622 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47623 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47624 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47625 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47626 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47627 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47628 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47629 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47630 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47631 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47632 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47633 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 33 | 47640 | Meter | Enum |  |  | The meter that this element is associated with
| 47641 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47642 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47643 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47644 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47645 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47646 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47647 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47648 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47649 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47650 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47651 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47652 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47653 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 34 | 47660 | Meter | Enum |  |  | The meter that this element is associated with
| 47661 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47662 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47663 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47664 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47665 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47666 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47667 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47668 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47669 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47670 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47671 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47672 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47673 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 35 | 47680 | Meter | Enum |  |  | The meter that this element is associated with
| 47681 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47682 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47683 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47684 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47685 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47686 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47687 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47688 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47689 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47690 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47691 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47692 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47693 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 36 | 47700 | Meter | Enum |  |  | The meter that this element is associated with
| 47701 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47702 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47703 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47704 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47705 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47706 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47707 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47708 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47709 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47710 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47711 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47712 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47713 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 37 | 47720 | Meter | Enum |  |  | The meter that this element is associated with
| 47721 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47722 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47723 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47724 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47725 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47726 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47727 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47728 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47729 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47730 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47731 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47732 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47733 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 38 | 47740 | Meter | Enum |  |  | The meter that this element is associated with
| 47741 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47742 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47743 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47744 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47745 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47746 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47747 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47748 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47749 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47750 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47751 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47752 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47753 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 39 | 47760 | Meter | Enum |  |  | The meter that this element is associated with
| 47761 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47762 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47763 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47764 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47765 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47766 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47767 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47768 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47769 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47770 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47771 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47772 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47773 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 40 | 47780 | Meter | Enum |  |  | The meter that this element is associated with
| 47781 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47782 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47783 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47784 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47785 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47786 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47787 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47788 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47789 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47790 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47791 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47792 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47793 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 41 | 47800 | Meter | Enum |  |  | The meter that this element is associated with
| 47801 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47802 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47803 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47804 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47805 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47806 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47807 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47808 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47809 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47810 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47811 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47812 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47813 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 42 | 47820 | Meter | Enum |  |  | The meter that this element is associated with
| 47821 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47822 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47823 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47824 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47825 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47826 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47827 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47828 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47829 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47830 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47831 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47832 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47833 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Element 43 | 47840 | Meter | Enum |  |  | The meter that this element is associated with
| 47841 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47842 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47843 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47844 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47845 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47846 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47847 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47848 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47849 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47850 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47851 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47852 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47853 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage A | 47860 | Meter | Enum |  |  | The meter that this element is associated with
| 47861 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47862 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47863 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47864 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47865 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47866 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47867 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47868 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47869 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47870 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47871 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47872 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47873 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage B | 47880 | Meter | Enum |  |  | The meter that this element is associated with
| 47881 | THD | UINT16 | 0.01% |  | Total harmonic distortion for this waverform
| 47882 | Fundamental | UINT16 | 0.01% |  | Fundamental component for this waveform
| 47883 | 2nd Harmonic | UINT16 | 0.01% |  | 2nd harmonic component for this waveform
| 47884 | 3rd Harmonic | UINT16 | 0.01% |  | 3rd harmonic component for this waveform
| 47885 | 4th Harmonic | UINT16 | 0.01% |  | 4th harmonic component for this waveform
| 47886 | 5th Harmonic | UINT16 | 0.01% |  | 5th harmonic component for this waveform
| 47887 | 6th Harmonic | UINT16 | 0.01% |  | 6th harmonic component for this waveform
| 47888 | 7th Harmonic | UINT16 | 0.01% |  | 7th harmonic component for this waveform
| 47889 | 8th Harmonic | UINT16 | 0.01% |  | 8th harmonic component for this waveform
| 47890 | 9th Harmonic | UINT16 | 0.01% |  | 9th harmonic component for this waveform
| 47891 | 10th Harmonic | UINT16 | 0.01% |  | 10th harmonic component for this waveform
| 47892 | 11th Harmonic | UINT16 | 0.01% |  | 11th harmonic component for this waveform
| 47893 | 12th Harmonic | UINT16 | 0.01% |  | 12th harmonic component for this waveform
Voltage C | 47900 | Meter | Enum |  |  | The meter that this element is associated with
| 49000 | Meter 1 Summary register (Main meter)
49017